## PTQMEMORY
Description | Start | Size
Supervisory Output from PLC to AFC | 400101 | 52
Supervisory Input to PLC from AFC | 400201 | 50
WallClock | 400291 | 6
Modbus Gateway | 400301 | 129
Modbus Pass-Thru | 400451 | 129
Modbus Master | 400601 | 130
Meter 1
Process Input from PLC to AFC | 400801 | 56
Calculations to PLC from AFC | 400901 | 38
Archive Fetch to PLC from AFC | 400951 | 42
Meter 2
Process Input from PLC to AFC | 401001 | 56
Calculations to PLC from AFC | 401101 | 38
Archive Fetch to PLC from AFC | 401151 | 42
Meter 3
Process Input from PLC to AFC | 401201 | 56
Calculations to PLC from AFC | 401301 | 38
Archive Fetch to PLC from AFC | 401351 | 42
Meter 4
Process Input from PLC to AFC | 401401 | 56
Calculations to PLC from AFC | 401501 | 38
Archive Fetch to PLC from AFC | 401551 | 42
Meter 5
Process Input from PLC to AFC | 401601 | 56
Calculations to PLC from AFC | 401701 | 38
Archive Fetch to PLC from AFC | 401751 | 42
Meter 6
Process Input from PLC to AFC | 401801 | 56
Calculations to PLC from AFC | 401901 | 38
Archive Fetch to PLC from AFC | 401951 | 42
Meter 7
Process Input from PLC to AFC | 402001 | 56
Calculations to PLC from AFC | 402101 | 38
Archive Fetch to PLC from AFC | 402151 | 42
Meter 8
Process Input from PLC to AFC | 402201 | 56
Calculations to PLC from AFC | 402301 | 38
Archive Fetch to PLC from AFC | 402351 | 42
Meter 9
Process Input from PLC to AFC | 402401 | 56
Calculations to PLC from AFC | 402501 | 38
Archive Fetch to PLC from AFC | 402551 | 42
Meter 10
Process Input from PLC to AFC | 402601 | 56
Calculations to PLC from AFC | 402701 | 38
Archive Fetch to PLC from AFC | 402751 | 42
Meter 11
Process Input from PLC to AFC | 402801 | 56
Calculations to PLC from AFC | 402901 | 38
Archive Fetch to PLC from AFC | 402951 | 42
Meter 12
Process Input from PLC to AFC | 403001 | 56
Calculations to PLC from AFC | 403101 | 38
Archive Fetch to PLC from AFC | 403151 | 42
Meter 13
Process Input from PLC to AFC | 403201 | 56
Calculations to PLC from AFC | 403301 | 38
Archive Fetch to PLC from AFC | 403351 | 42
Meter 14
Process Input from PLC to AFC | 403401 | 56
Calculations to PLC from AFC | 403501 | 38
Archive Fetch to PLC from AFC | 403551 | 42
Meter 15
Process Input from PLC to AFC | 403601 | 56
Calculations to PLC from AFC | 403701 | 38
Archive Fetch to PLC from AFC | 403751 | 42
Meter 16
Process Input from PLC to AFC | 403801 | 56
Calculations to PLC from AFC | 403901 | 38
Archive Fetch to PLC from AFC | 403951 | 42
TOTAL |  | 2672

## SupervisoryOutput
Supervisory Block Output Structure
Offset | Description | Word Address | Comments | Test
0 | Set Wallclock | 400101 |  | Y
1 | Read WallClock | 400102 |  | Y
2 | Issue Gateway Transaction | 400103
3 | Fetch Pass-Thru Transaction | 400104
4 | Issue Master Transaction | 400105
5 | Reserved | 400106
6 | Reserved | 400107
7 | Reserved | 400108
8 | Reserved | 400109
9 | Reserved | 400110
10 | Pass-Thru Ack | 400111
11 | Pass-Thru Swap Words | 400112
12 | Reserved | 400113
13 | Reserved | 400114
14 | Reserved | 400115
15 | Reserved | 400116
16 | Reserved | 400117
17 | Reserved | 400118
18 | Reserved | 400119
19 | Reserved | 400120
20 | Site Signals / Event Log Download Complete | 400121
21 | Site Signals / Clear All CheckSum Alarms | 400122
22 | Reserved | 400123
23 | Reserved | 400124
24 | Reserved | 400125
25 | Reserved | 400126
26 | Reserved | 400127
27 | Reserved | 400128
28 | Reserved | 400129
29 | Reserved | 400130
30 | Reserved | 400131
31 | Reserved | 400132
32 | Reserved | 400133
33 | Reserved | 400134
34 | Reserved | 400135
35 | Reserved | 400136
36 | Enable Meter 1 | 400137
37 | Enable Meter 2 | 400138
38 | Enable Meter 3 | 400139
39 | Enable Meter 4 | 400140
40 | Enable Meter 5 | 400141
41 | Enable Meter 6 | 400142
42 | Enable Meter 7 | 400143
43 | Enable Meter 8 | 400144
44 | Enable Meter 9 | 400145
45 | Enable Meter 10 | 400146
46 | Enable Meter 11 | 400147
47 | Enable Meter 12 | 400148
48 | Enable Meter 13 | 400149
49 | Enable Meter 14 | 400150
50 | Enable Meter 15 | 400151
51 | Enable Meter 16 | 400152

## SupervisoryInput
Supervisory Block Input Structure
Offset | Description | Word Address | Comments
0 | Wallclock set fail | 400201
1 | Event log full error | 400202
2 | Master transaction logic error | 400203
3 | Reserved | 400204
4 | Reserved | 400205
5 | Reserved | 400206
6 | Reserved | 400207
7 | Reserved | 400208
8 | Reserved | 400209
9 | Reserved | 400210
10 | Wallclock not set | 400211
11 | Meter in alarm | 400212 | Bit 0 = Alarm Meter 1 , Bit 1 = Alarm Meter 2, etc…
12 | Pass-thru transaction pending | 400213
13 | Reserved | 400214
14 | Reserved | 400215
15 | Reserved | 400216
16 | Reserved | 400217
17 | Reserved | 400218
18 | Reserved | 400219
19 | Reserved | 400220
20 | PTQ-AFC Released | 400221
21 | Reserved | 400222
22 | Reserved | 400223
23 | Reserved | 400224
24 | Quantum halted, offline, or missing | 400225
25 | Measurement configuration changed | 400226
26 | Power up | 400227
27 | Cold start | 400228
28 | Reserved | 400229
29 | Reserved | 400230
30 | Meter 1 Information | 400231 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
31 | Meter 2 Information | 400232 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
32 | Meter 3 Information | 400233 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
33 | Meter 4 Information | 400234 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
34 | Meter 5 Information | 400235 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
35 | Meter 6 Information | 400236 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
36 | Meter 7 Information | 400237 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
37 | Meter 8 Information | 400238 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
38 | Meter 9 Information | 400239 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
39 | Meter 10 Information | 400240 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
40 | Meter 11 Information | 400241 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
41 | Meter 12 Information | 400242 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
42 | Meter 13 Information | 400243 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
43 | Meter 14 Information | 400244 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
44 | Meter 15 Information | 400245 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
45 | Meter 16 Information | 400246 | Bit 0: meter is in alarm, Bit 1: meter enabled, Bit 4: Linear, Bit 5: liquid, Bit 6 integration, Bit 8 stream 1 enabled, Bit 9 stream 2 enabled, Bit 10 stream 3 enabled, Bit 11 stream 4 enabled, Bits 12 thru 13 active stream number (0 thru 3)
46 | Scan Count | 400247
47 | Pass-Thru Transaction word/bit select | 400248
48 | Pass-Thru Transaction register address | 400249
49 | Pass-Thru Transaction number of registers | 400250

## WallClock
Wallclock Block Structure
Offset | Description | Word Address | Comments
0 | Year | 400291
1 | Month | 400292
2 | Day | 400293
3 | Hour | 400294
4 | Minute | 400295
5 | Second | 400296

## Modbus Gateway
Modbus Gateway Block Structure
Offset | Description | Word Address | Comments
0 | Slave Selection, register bank, direction | 400301 | See User Manual
1 | Register address | 400302
2 | Number of registers | 400303
3 | Modbus exception code | 400304
4 | Data | 400305
5 | Data | 400306
6 | Data | 400307
7 | Data | 400308
8 | Data | 400309
9 | Data | 400310
10 | Data | 400311
11 | Data | 400312
12 | Data | 400313
13 | Data | 400314
14 | Data | 400315
15 | Data | 400316
16 | Data | 400317
17 | Data | 400318
18 | Data | 400319
19 | Data | 400320
20 | Data | 400321
21 | Data | 400322
22 | Data | 400323
23 | Data | 400324
24 | Data | 400325
25 | Data | 400326
26 | Data | 400327
27 | Data | 400328
28 | Data | 400329
29 | Data | 400330
30 | Data | 400331
31 | Data | 400332
32 | Data | 400333
33 | Data | 400334
34 | Data | 400335
35 | Data | 400336
36 | Data | 400337
37 | Data | 400338
38 | Data | 400339
39 | Data | 400340
40 | Data | 400341
41 | Data | 400342
42 | Data | 400343
43 | Data | 400344
44 | Data | 400345
45 | Data | 400346
46 | Data | 400347
47 | Data | 400348
48 | Data | 400349
49 | Data | 400350
50 | Data | 400351
51 | Data | 400352
52 | Data | 400353
53 | Data | 400354
54 | Data | 400355
55 | Data | 400356
56 | Data | 400357
57 | Data | 400358
58 | Data | 400359
59 | Data | 400360
60 | Data | 400361
61 | Data | 400362
62 | Data | 400363
63 | Data | 400364
64 | Data | 400365
65 | Data | 400366
66 | Data | 400367
67 | Data | 400368
68 | Data | 400369
69 | Data | 400370
70 | Data | 400371
71 | Data | 400372
72 | Data | 400373
73 | Data | 400374
74 | Data | 400375
75 | Data | 400376
76 | Data | 400377
77 | Data | 400378
78 | Data | 400379
79 | Data | 400380
80 | Data | 400381
81 | Data | 400382
82 | Data | 400383
83 | Data | 400384
84 | Data | 400385
85 | Data | 400386
86 | Data | 400387
87 | Data | 400388
88 | Data | 400389
89 | Data | 400390
90 | Data | 400391
91 | Data | 400392
92 | Data | 400393
93 | Data | 400394
94 | Data | 400395
95 | Data | 400396
96 | Data | 400397
97 | Data | 400398
98 | Data | 400399
99 | Data | 400400
100 | Data | 400401
101 | Data | 400402
102 | Data | 400403
103 | Data | 400404
104 | Data | 400405
105 | Data | 400406
106 | Data | 400407
107 | Data | 400408
108 | Data | 400409
109 | Data | 400410
110 | Data | 400411
111 | Data | 400412
112 | Data | 400413
113 | Data | 400414
114 | Data | 400415
115 | Data | 400416
116 | Data | 400417
117 | Data | 400418
118 | Data | 400419
119 | Data | 400420
120 | Data | 400421
121 | Data | 400422
122 | Data | 400423
123 | Data | 400424
124 | Data | 400425
125 | Data | 400426

## Modbus Pass-Thru
Modbus Pass-Thru Block Structure
Offset | Description | Word Address | Comments
0 | Pass-Thru transaction pending | 400451
1 | Pass-Thru transaction word/bit select | 400452 | 0=word, 1=bit
2 | Register Address | 400453
3 | Number of Registers | 400454
4 | Data | 400455
5 | Data | 400456
6 | Data | 400457
7 | Data | 400458
8 | Data | 400459
9 | Data | 400460
10 | Data | 400461
11 | Data | 400462
12 | Data | 400463
13 | Data | 400464
14 | Data | 400465
15 | Data | 400466
16 | Data | 400467
17 | Data | 400468
18 | Data | 400469
19 | Data | 400470
20 | Data | 400471
21 | Data | 400472
22 | Data | 400473
23 | Data | 400474
24 | Data | 400475
25 | Data | 400476
26 | Data | 400477
27 | Data | 400478
28 | Data | 400479
29 | Data | 400480
30 | Data | 400481
31 | Data | 400482
32 | Data | 400483
33 | Data | 400484
34 | Data | 400485
35 | Data | 400486
36 | Data | 400487
37 | Data | 400488
38 | Data | 400489
39 | Data | 400490
40 | Data | 400491
41 | Data | 400492
42 | Data | 400493
43 | Data | 400494
44 | Data | 400495
45 | Data | 400496
46 | Data | 400497
47 | Data | 400498
48 | Data | 400499
49 | Data | 400500
50 | Data | 400501
51 | Data | 400502
52 | Data | 400503
53 | Data | 400504
54 | Data | 400505
55 | Data | 400506
56 | Data | 400507
57 | Data | 400508
58 | Data | 400509
59 | Data | 400510
60 | Data | 400511
61 | Data | 400512
62 | Data | 400513
63 | Data | 400514
64 | Data | 400515
65 | Data | 400516
66 | Data | 400517
67 | Data | 400518
68 | Data | 400519
69 | Data | 400520
70 | Data | 400521
71 | Data | 400522
72 | Data | 400523
73 | Data | 400524
74 | Data | 400525
75 | Data | 400526
76 | Data | 400527
77 | Data | 400528
78 | Data | 400529
79 | Data | 400530
80 | Data | 400531
81 | Data | 400532
82 | Data | 400533
83 | Data | 400534
84 | Data | 400535
85 | Data | 400536
86 | Data | 400537
87 | Data | 400538
88 | Data | 400539
89 | Data | 400540
90 | Data | 400541
91 | Data | 400542
92 | Data | 400543
93 | Data | 400544
94 | Data | 400545
95 | Data | 400546
96 | Data | 400547
97 | Data | 400548
98 | Data | 400549
99 | Data | 400550
100 | Data | 400551
101 | Data | 400552
102 | Data | 400553
103 | Data | 400554
104 | Data | 400555
105 | Data | 400556
106 | Data | 400557
107 | Data | 400558
108 | Data | 400559
109 | Data | 400560
110 | Data | 400561
111 | Data | 400562
112 | Data | 400563
113 | Data | 400564
114 | Data | 400565
115 | Data | 400566
116 | Data | 400567
117 | Data | 400568
118 | Data | 400569
119 | Data | 400570
120 | Data | 400571
121 | Data | 400572
122 | Data | 400573
123 | Data | 400574
124 | Data | 400575
125 | Data | 400576

## Modbus Master
Modbus Master Block Structure
Offset | Description | Word Address | Comments
0 | Slave Address | 400601 | See User Manual
1 | Direction and register bank | 400602
2 | Data Item Size and Swap Options | 400603
3 | Register Address | 400604 | See User Manual
4 | Number of Data Items | 400605
5 | Error Code | 400606 | See User Manual
6 | Data | 400607
7 | Data | 400608
8 | Data | 400609
9 | Data | 400610
10 | Data | 400611
11 | Data | 400612
12 | Data | 400613
13 | Data | 400614
14 | Data | 400615
15 | Data | 400616
16 | Data | 400617
17 | Data | 400618
18 | Data | 400619
19 | Data | 400620
20 | Data | 400621
21 | Data | 400622
22 | Data | 400623
23 | Data | 400624
24 | Data | 400625
25 | Data | 400626
26 | Data | 400627
27 | Data | 400628
28 | Data | 400629
29 | Data | 400630
30 | Data | 400631
31 | Data | 400632
32 | Data | 400633
33 | Data | 400634
34 | Data | 400635
35 | Data | 400636
36 | Data | 400637
37 | Data | 400638
38 | Data | 400639
39 | Data | 400640
40 | Data | 400641
41 | Data | 400642
42 | Data | 400643
43 | Data | 400644
44 | Data | 400645
45 | Data | 400646
46 | Data | 400647
47 | Data | 400648
48 | Data | 400649
49 | Data | 400650
50 | Data | 400651
51 | Data | 400652
52 | Data | 400653
53 | Data | 400654
54 | Data | 400655
55 | Data | 400656
56 | Data | 400657
57 | Data | 400658
58 | Data | 400659
59 | Data | 400660
60 | Data | 400661
61 | Data | 400662
62 | Data | 400663
63 | Data | 400664
64 | Data | 400665
65 | Data | 400666
66 | Data | 400667
67 | Data | 400668
68 | Data | 400669
69 | Data | 400670
70 | Data | 400671
71 | Data | 400672
72 | Data | 400673
73 | Data | 400674
74 | Data | 400675
75 | Data | 400676
76 | Data | 400677
77 | Data | 400678
78 | Data | 400679
79 | Data | 400680
80 | Data | 400681
81 | Data | 400682
82 | Data | 400683
83 | Data | 400684
84 | Data | 400685
85 | Data | 400686
86 | Data | 400687
87 | Data | 400688
88 | Data | 400689
89 | Data | 400690
90 | Data | 400691
91 | Data | 400692
92 | Data | 400693
93 | Data | 400694
94 | Data | 400695
95 | Data | 400696
96 | Data | 400697
97 | Data | 400698
98 | Data | 400699
99 | Data | 400700
100 | Data | 400701
101 | Data | 400702
102 | Data | 400703
103 | Data | 400704
104 | Data | 400705
105 | Data | 400706
106 | Data | 400707
107 | Data | 400708
108 | Data | 400709
109 | Data | 400710
110 | Data | 400711
111 | Data | 400712
112 | Data | 400713
113 | Data | 400714
114 | Data | 400715
115 | Data | 400716
116 | Data | 400717
117 | Data | 400718
118 | Data | 400719
119 | Data | 400720
120 | Data | 400721
121 | Data | 400722
122 | Data | 400723
123 | Data | 400724
124 | Data | 400725

## Meter Variables - Orifice & Gas
Meter 1 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Meter Disable | 400801
1 | 1 | Reserved | 400802
2 | 1 | Temperature | 400803 | Floating Point Format
3 | 1 | Temperature | 400804 | Floating Point Format
4 | 1 | Pressure | 400805 | Floating Point Format
5 | 1 | Pressure | 400806 | Floating Point Format
6 | 1 | Differential Pressure | 400807 | Floating Point Format
7 | 1 | Differential Pressure | 400808 | Floating Point Format
8 | 1 | Reserved | 400809
9 | 1 | Reserved | 400810
10 | 1 | Reserved | 400811
11 | 1 | Reserved | 400812
12 | 1 | Molar Analysis - C1 | 400813 | Scaled Integer Format (10000 = 100%)
13 | 1 | Molar Analysis - N2 | 400814 | Scaled Integer Format (10000 = 100%)
14 | 1 | Molar Analysis - CO2 | 400815 | Scaled Integer Format (10000 = 100%)
15 | 1 | Molar Analysis - C2 | 400816 | Scaled Integer Format (10000 = 100%)
16 | 1 | Molar Analysis - C3 | 400817 | Scaled Integer Format (10000 = 100%)
17 | 1 | Molar Analysis - H2O | 400818 | Scaled Integer Format (10000 = 100%)
18 | 1 | Molar Analysis - H2S | 400819 | Scaled Integer Format (10000 = 100%)
19 | 1 | Molar Analysis - H2 | 400820 | Scaled Integer Format (10000 = 100%)
20 | 1 | Molar Analysis - CO | 400821 | Scaled Integer Format (10000 = 100%)
21 | 1 | Molar Analysis - O2 | 400822 | Scaled Integer Format (10000 = 100%)
22 | 1 | Molar Analysis - iC4 | 400823 | Scaled Integer Format (10000 = 100%)
23 | 1 | Molar Analysis - C4 | 400824 | Scaled Integer Format (10000 = 100%)
24 | 1 | Molar Analysis - iC5 | 400825 | Scaled Integer Format (10000 = 100%)
25 | 1 | Molar Analysis - C5 | 400826 | Scaled Integer Format (10000 = 100%)
26 | 1 | Molar Analysis - C6 | 400827 | Scaled Integer Format (10000 = 100%)
27 | 1 | Molar Analysis - C7 | 400828 | Scaled Integer Format (10000 = 100%)
28 | 1 | Molar Analysis - C8 | 400829 | Scaled Integer Format (10000 = 100%)
29 | 1 | Molar Analysis - C9 | 400830 | Scaled Integer Format (10000 = 100%)
30 | 1 | Molar Analysis - C10 | 400831 | Scaled Integer Format (10000 = 100%)
31 | 1 | Molar Analysis - He | 400832 | Scaled Integer Format (10000 = 100%)
32 | 1 | Molar Analysis - Ar | 400833 | Scaled Integer Format (10000 = 100%)
33 | 1 | Molar Analysis - C5 (neo-p) | 400834 | Scaled Integer Format (10000 = 100%)
34 | 1 | Molar Analysis - Ux | 400835 | Scaled Integer Format (10000 = 100%)
35 | 1 | Molar Analysis - Uy | 400836 | Scaled Integer Format (10000 = 100%)
36 | 1 | Meter Signals - SelectStream1 | 400837
37 | 1 | Meter Signals - SelectStream2 | 400838
38 | 1 | Meter Signals - SelectStream3 | 400839
39 | 1 | Meter Signals - SelectStream4 | 400840
40 | 1 | Meter Signals - Reset Acc 1 | 400841
41 | 1 | Meter Signals - Reset Acc 2 | 400842
42 | 1 | Meter Signals - Reset Acc 3 | 400843
43 | 1 | Meter Signals - Reset Acc 4 | 400844
44 | 1 | Write Daily Archive | 400845
45 | 1 | Write Hourly Archive | 400846
46 | 1 | Meter Signals - Reserved | 400847
47 | 1 | Meter Signals - Reserved | 400848
48 | 1 | Meter Signals - Reserved | 400849
49 | 1 | Meter Signals - Reserved | 400850
50 | 1 | Meter Signals - Reserved | 400851
51 | 1 | Meter Signals - Reserved | 400852
52 | 1 | Analysis is Present | 400853
53 | 1 | Meter Archive Record Fetch | 400854 | (=0 signal not present)
54 | 1 | Meter Archive Record Age | 400855 | (=0 current)
55 | 1 | Meter Archive File Select | 400856 | (=0 daily, 1=hourly)
Meter 2 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Meter Disable | 401001
1 | 2 | Reserved | 401002
2 | 2 | Temperature | 401003 | Floating Point Format
3 | 2 | Temperature | 401004 | Floating Point Format
4 | 2 | Pressure | 401005 | Floating Point Format
5 | 2 | Pressure | 401006 | Floating Point Format
6 | 2 | Differential Pressure | 401007 | Floating Point Format
7 | 2 | Differential Pressure | 401008 | Floating Point Format
8 | 2 | Reserved | 401009
9 | 2 | Reserved | 401010
10 | 2 | Reserved | 401011
11 | 2 | Reserved | 401012
12 | 2 | Molar Analysis - C1 | 401013 | Scaled Integer Format (10000 = 100%)
13 | 2 | Molar Analysis - N2 | 401014 | Scaled Integer Format (10000 = 100%)
14 | 2 | Molar Analysis - CO2 | 401015 | Scaled Integer Format (10000 = 100%)
15 | 2 | Molar Analysis - C2 | 401016 | Scaled Integer Format (10000 = 100%)
16 | 2 | Molar Analysis - C3 | 401017 | Scaled Integer Format (10000 = 100%)
17 | 2 | Molar Analysis - H2O | 401018 | Scaled Integer Format (10000 = 100%)
18 | 2 | Molar Analysis - H2S | 401019 | Scaled Integer Format (10000 = 100%)
19 | 2 | Molar Analysis - H2 | 401020 | Scaled Integer Format (10000 = 100%)
20 | 2 | Molar Analysis - CO | 401021 | Scaled Integer Format (10000 = 100%)
21 | 2 | Molar Analysis - O2 | 401022 | Scaled Integer Format (10000 = 100%)
22 | 2 | Molar Analysis - iC4 | 401023 | Scaled Integer Format (10000 = 100%)
23 | 2 | Molar Analysis - C4 | 401024 | Scaled Integer Format (10000 = 100%)
24 | 2 | Molar Analysis - iC5 | 401025 | Scaled Integer Format (10000 = 100%)
25 | 2 | Molar Analysis - C5 | 401026 | Scaled Integer Format (10000 = 100%)
26 | 2 | Molar Analysis - C6 | 401027 | Scaled Integer Format (10000 = 100%)
27 | 2 | Molar Analysis - C7 | 401028 | Scaled Integer Format (10000 = 100%)
28 | 2 | Molar Analysis - C8 | 401029 | Scaled Integer Format (10000 = 100%)
29 | 2 | Molar Analysis - C9 | 401030 | Scaled Integer Format (10000 = 100%)
30 | 2 | Molar Analysis - C10 | 401031 | Scaled Integer Format (10000 = 100%)
31 | 2 | Molar Analysis - He | 401032 | Scaled Integer Format (10000 = 100%)
32 | 2 | Molar Analysis - Ar | 401033 | Scaled Integer Format (10000 = 100%)
33 | 2 | Molar Analysis - C5 (neo-p) | 401034 | Scaled Integer Format (10000 = 100%)
34 | 2 | Molar Analysis - Ux | 401035 | Scaled Integer Format (10000 = 100%)
35 | 2 | Molar Analysis - Uy | 401036 | Scaled Integer Format (10000 = 100%)
36 | 2 | Meter Signals - Reserved | 401037
37 | 2 | Meter Signals - Reserved | 401038
38 | 2 | Meter Signals - Reserved | 401039
39 | 2 | Meter Signals - Reserved | 401040
40 | 2 | Meter Signals - Reset Acc 1 | 401041
41 | 2 | Meter Signals - Reset Acc 2 | 401042
42 | 2 | Meter Signals - Reset Acc 3 | 401043
43 | 2 | Meter Signals - Reset Acc 4 | 401044
44 | 2 | Write Daily Archive | 401045
45 | 2 | Write Hourly Archive | 401046
46 | 2 | Meter Signals - Reserved | 401047
47 | 2 | Meter Signals - Reserved | 401048
48 | 2 | Meter Signals - Reserved | 401049
49 | 2 | Meter Signals - Reserved | 401050
50 | 2 | Meter Signals - Reserved | 401051
51 | 2 | Meter Signals - Reserved | 401052
52 | 2 | Analysis is Present | 401053
53 | 2 | Meter Archive Record Fetch | 401054 | (=0 signal not present)
54 | 2 | Meter Archive Record Age | 401055 | (=0 current)
55 | 2 | Meter Archive File Select | 401056 | (=0 daily, 1=hourly)
Meter 3 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Meter Disable | 401201
1 | 3 | Reserved | 401202
2 | 3 | Temperature | 401203 | Floating Point Format
3 | 3 | Temperature | 401204 | Floating Point Format
4 | 3 | Pressure | 401205 | Floating Point Format
5 | 3 | Pressure | 401206 | Floating Point Format
6 | 3 | Differential Pressure | 401207 | Floating Point Format
7 | 3 | Differential Pressure | 401208 | Floating Point Format
8 | 3 | Reserved | 401209
9 | 3 | Reserved | 401210
10 | 3 | Reserved | 401211
11 | 3 | Reserved | 401212
12 | 3 | Molar Analysis - C1 | 401213 | Scaled Integer Format (10000 = 100%)
13 | 3 | Molar Analysis - N2 | 401214 | Scaled Integer Format (10000 = 100%)
14 | 3 | Molar Analysis - CO2 | 401215 | Scaled Integer Format (10000 = 100%)
15 | 3 | Molar Analysis - C2 | 401216 | Scaled Integer Format (10000 = 100%)
16 | 3 | Molar Analysis - C3 | 401217 | Scaled Integer Format (10000 = 100%)
17 | 3 | Molar Analysis - H2O | 401218 | Scaled Integer Format (10000 = 100%)
18 | 3 | Molar Analysis - H2S | 401219 | Scaled Integer Format (10000 = 100%)
19 | 3 | Molar Analysis - H2 | 401220 | Scaled Integer Format (10000 = 100%)
20 | 3 | Molar Analysis - CO | 401221 | Scaled Integer Format (10000 = 100%)
21 | 3 | Molar Analysis - O2 | 401222 | Scaled Integer Format (10000 = 100%)
22 | 3 | Molar Analysis - iC4 | 401223 | Scaled Integer Format (10000 = 100%)
23 | 3 | Molar Analysis - C4 | 401224 | Scaled Integer Format (10000 = 100%)
24 | 3 | Molar Analysis - iC5 | 401225 | Scaled Integer Format (10000 = 100%)
25 | 3 | Molar Analysis - C5 | 401226 | Scaled Integer Format (10000 = 100%)
26 | 3 | Molar Analysis - C6 | 401227 | Scaled Integer Format (10000 = 100%)
27 | 3 | Molar Analysis - C7 | 401228 | Scaled Integer Format (10000 = 100%)
28 | 3 | Molar Analysis - C8 | 401229 | Scaled Integer Format (10000 = 100%)
29 | 3 | Molar Analysis - C9 | 401230 | Scaled Integer Format (10000 = 100%)
30 | 3 | Molar Analysis - C10 | 401231 | Scaled Integer Format (10000 = 100%)
31 | 3 | Molar Analysis - He | 401232 | Scaled Integer Format (10000 = 100%)
32 | 3 | Molar Analysis - Ar | 401233 | Scaled Integer Format (10000 = 100%)
33 | 3 | Molar Analysis - C5 (neo-p) | 401234 | Scaled Integer Format (10000 = 100%)
34 | 3 | Molar Analysis - Ux | 401235 | Scaled Integer Format (10000 = 100%)
35 | 3 | Molar Analysis - Uy | 401236 | Scaled Integer Format (10000 = 100%)
36 | 3 | Meter Signals - Reserved | 401237
37 | 3 | Meter Signals - Reserved | 401238
38 | 3 | Meter Signals - Reserved | 401239
39 | 3 | Meter Signals - Reserved | 401240
40 | 3 | Meter Signals - Reset Acc 1 | 401241
41 | 3 | Meter Signals - Reset Acc 2 | 401242
42 | 3 | Meter Signals - Reset Acc 3 | 401243
43 | 3 | Meter Signals - Reset Acc 4 | 401244
44 | 3 | Write Daily Archive | 401245
45 | 3 | Write Hourly Archive | 401246
46 | 3 | Meter Signals - Reserved | 401247
47 | 3 | Meter Signals - Reserved | 401248
48 | 3 | Meter Signals - Reserved | 401249
49 | 3 | Meter Signals - Reserved | 401250
50 | 3 | Meter Signals - Reserved | 401251
51 | 3 | Meter Signals - Reserved | 401252
52 | 3 | Analysis is Present | 401253
53 | 3 | Meter Archive Record Fetch | 401254 | (=0 signal not present)
54 | 3 | Meter Archive Record Age | 401255 | (=0 current)
55 | 3 | Meter Archive File Select | 401256 | (=0 daily, 1=hourly)
Meter 4 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Meter Disable | 401401
1 | 4 | Reserved | 401402
2 | 4 | Temperature | 401403 | Floating Point Format
3 | 4 | Temperature | 401404 | Floating Point Format
4 | 4 | Pressure | 401405 | Floating Point Format
5 | 4 | Pressure | 401406 | Floating Point Format
6 | 4 | Differential Pressure | 401407 | Floating Point Format
7 | 4 | Differential Pressure | 401408 | Floating Point Format
8 | 4 | Reserved | 401409
9 | 4 | Reserved | 401410
10 | 4 | Reserved | 401411
11 | 4 | Reserved | 401412
12 | 4 | Molar Analysis - C1 | 401413 | Scaled Integer Format (10000 = 100%)
13 | 4 | Molar Analysis - N2 | 401414 | Scaled Integer Format (10000 = 100%)
14 | 4 | Molar Analysis - CO2 | 401415 | Scaled Integer Format (10000 = 100%)
15 | 4 | Molar Analysis - C2 | 401416 | Scaled Integer Format (10000 = 100%)
16 | 4 | Molar Analysis - C3 | 401417 | Scaled Integer Format (10000 = 100%)
17 | 4 | Molar Analysis - H2O | 401418 | Scaled Integer Format (10000 = 100%)
18 | 4 | Molar Analysis - H2S | 401419 | Scaled Integer Format (10000 = 100%)
19 | 4 | Molar Analysis - H2 | 401420 | Scaled Integer Format (10000 = 100%)
20 | 4 | Molar Analysis - CO | 401421 | Scaled Integer Format (10000 = 100%)
21 | 4 | Molar Analysis - O2 | 401422 | Scaled Integer Format (10000 = 100%)
22 | 4 | Molar Analysis - iC4 | 401423 | Scaled Integer Format (10000 = 100%)
23 | 4 | Molar Analysis - C4 | 401424 | Scaled Integer Format (10000 = 100%)
24 | 4 | Molar Analysis - iC5 | 401425 | Scaled Integer Format (10000 = 100%)
25 | 4 | Molar Analysis - C5 | 401426 | Scaled Integer Format (10000 = 100%)
26 | 4 | Molar Analysis - C6 | 401427 | Scaled Integer Format (10000 = 100%)
27 | 4 | Molar Analysis - C7 | 401428 | Scaled Integer Format (10000 = 100%)
28 | 4 | Molar Analysis - C8 | 401429 | Scaled Integer Format (10000 = 100%)
29 | 4 | Molar Analysis - C9 | 401430 | Scaled Integer Format (10000 = 100%)
30 | 4 | Molar Analysis - C10 | 401431 | Scaled Integer Format (10000 = 100%)
31 | 4 | Molar Analysis - He | 401432 | Scaled Integer Format (10000 = 100%)
32 | 4 | Molar Analysis - Ar | 401433 | Scaled Integer Format (10000 = 100%)
33 | 4 | Molar Analysis - C5 (neo-p) | 401434 | Scaled Integer Format (10000 = 100%)
34 | 4 | Molar Analysis - Ux | 401435 | Scaled Integer Format (10000 = 100%)
35 | 4 | Molar Analysis - Uy | 401436 | Scaled Integer Format (10000 = 100%)
36 | 4 | Meter Signals - Reserved | 401437
37 | 4 | Meter Signals - Reserved | 401438
38 | 4 | Meter Signals - Reserved | 401439
39 | 4 | Meter Signals - Reserved | 401440
40 | 4 | Meter Signals - Reset Acc 1 | 401441
41 | 4 | Meter Signals - Reset Acc 2 | 401442
42 | 4 | Meter Signals - Reset Acc 3 | 401443
43 | 4 | Meter Signals - Reset Acc 4 | 401444
44 | 4 | Write Daily Archive | 401445
45 | 4 | Write Hourly Archive | 401446
46 | 4 | Meter Signals - Reserved | 401447
47 | 4 | Meter Signals - Reserved | 401448
48 | 4 | Meter Signals - Reserved | 401449
49 | 4 | Meter Signals - Reserved | 401450
50 | 4 | Meter Signals - Reserved | 401451
51 | 4 | Meter Signals - Reserved | 401452
52 | 4 | Analysis is Present | 401453
53 | 4 | Meter Archive Record Fetch | 401454 | (=0 signal not present)
54 | 4 | Meter Archive Record Age | 401455 | (=0 current)
55 | 4 | Meter Archive File Select | 401456 | (=0 daily, 1=hourly)
Meter 5 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Meter Disable | 401601
1 | 5 | Reserved | 401602
2 | 5 | Temperature | 401603 | Floating Point Format
3 | 5 | Temperature | 401604 | Floating Point Format
4 | 5 | Pressure | 401605 | Floating Point Format
5 | 5 | Pressure | 401606 | Floating Point Format
6 | 5 | Differential Pressure | 401607 | Floating Point Format
7 | 5 | Differential Pressure | 401608 | Floating Point Format
8 | 5 | Reserved | 401609
9 | 5 | Reserved | 401610
10 | 5 | Reserved | 401611
11 | 5 | Reserved | 401612
12 | 5 | Molar Analysis - C1 | 401613 | Scaled Integer Format (10000 = 100%)
13 | 5 | Molar Analysis - N2 | 401614 | Scaled Integer Format (10000 = 100%)
14 | 5 | Molar Analysis - CO2 | 401615 | Scaled Integer Format (10000 = 100%)
15 | 5 | Molar Analysis - C2 | 401616 | Scaled Integer Format (10000 = 100%)
16 | 5 | Molar Analysis - C3 | 401617 | Scaled Integer Format (10000 = 100%)
17 | 5 | Molar Analysis - H2O | 401618 | Scaled Integer Format (10000 = 100%)
18 | 5 | Molar Analysis - H2S | 401619 | Scaled Integer Format (10000 = 100%)
19 | 5 | Molar Analysis - H2 | 401620 | Scaled Integer Format (10000 = 100%)
20 | 5 | Molar Analysis - CO | 401621 | Scaled Integer Format (10000 = 100%)
21 | 5 | Molar Analysis - O2 | 401622 | Scaled Integer Format (10000 = 100%)
22 | 5 | Molar Analysis - iC4 | 401623 | Scaled Integer Format (10000 = 100%)
23 | 5 | Molar Analysis - C4 | 401624 | Scaled Integer Format (10000 = 100%)
24 | 5 | Molar Analysis - iC5 | 401625 | Scaled Integer Format (10000 = 100%)
25 | 5 | Molar Analysis - C5 | 401626 | Scaled Integer Format (10000 = 100%)
26 | 5 | Molar Analysis - C6 | 401627 | Scaled Integer Format (10000 = 100%)
27 | 5 | Molar Analysis - C7 | 401628 | Scaled Integer Format (10000 = 100%)
28 | 5 | Molar Analysis - C8 | 401629 | Scaled Integer Format (10000 = 100%)
29 | 5 | Molar Analysis - C9 | 401630 | Scaled Integer Format (10000 = 100%)
30 | 5 | Molar Analysis - C10 | 401631 | Scaled Integer Format (10000 = 100%)
31 | 5 | Molar Analysis - He | 401632 | Scaled Integer Format (10000 = 100%)
32 | 5 | Molar Analysis - Ar | 401633 | Scaled Integer Format (10000 = 100%)
33 | 5 | Molar Analysis - C5 (neo-p) | 401634 | Scaled Integer Format (10000 = 100%)
34 | 5 | Molar Analysis - Ux | 401635 | Scaled Integer Format (10000 = 100%)
35 | 5 | Molar Analysis - Uy | 401636 | Scaled Integer Format (10000 = 100%)
36 | 5 | Meter Signals - Reserved | 401637
37 | 5 | Meter Signals - Reserved | 401638
38 | 5 | Meter Signals - Reserved | 401639
39 | 5 | Meter Signals - Reserved | 401640
40 | 5 | Meter Signals - Reset Acc 1 | 401641
41 | 5 | Meter Signals - Reset Acc 2 | 401642
42 | 5 | Meter Signals - Reset Acc 3 | 401643
43 | 5 | Meter Signals - Reset Acc 4 | 401644
44 | 5 | Write Daily Archive | 401645
45 | 5 | Write Hourly Archive | 401646
46 | 5 | Meter Signals - Reserved | 401647
47 | 5 | Meter Signals - Reserved | 401648
48 | 5 | Meter Signals - Reserved | 401649
49 | 5 | Meter Signals - Reserved | 401650
50 | 5 | Meter Signals - Reserved | 401651
51 | 5 | Meter Signals - Reserved | 401652
52 | 5 | Analysis is Present | 401653
53 | 5 | Meter Archive Record Fetch | 401654 | (=0 signal not present)
54 | 5 | Meter Archive Record Age | 401655 | (=0 current)
55 | 5 | Meter Archive File Select | 401656 | (=0 daily, 1=hourly)
Meter 6 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Meter Disable | 401801
1 | 6 | Reserved | 401802
2 | 6 | Temperature | 401803 | Floating Point Format
3 | 6 | Temperature | 401804 | Floating Point Format
4 | 6 | Pressure | 401805 | Floating Point Format
5 | 6 | Pressure | 401806 | Floating Point Format
6 | 6 | Differential Pressure | 401807 | Floating Point Format
7 | 6 | Differential Pressure | 401808 | Floating Point Format
8 | 6 | Reserved | 401809
9 | 6 | Reserved | 401810
10 | 6 | Reserved | 401811
11 | 6 | Reserved | 401812
12 | 6 | Molar Analysis - C1 | 401813 | Scaled Integer Format (10000 = 100%)
13 | 6 | Molar Analysis - N2 | 401814 | Scaled Integer Format (10000 = 100%)
14 | 6 | Molar Analysis - CO2 | 401815 | Scaled Integer Format (10000 = 100%)
15 | 6 | Molar Analysis - C2 | 401816 | Scaled Integer Format (10000 = 100%)
16 | 6 | Molar Analysis - C3 | 401817 | Scaled Integer Format (10000 = 100%)
17 | 6 | Molar Analysis - H2O | 401818 | Scaled Integer Format (10000 = 100%)
18 | 6 | Molar Analysis - H2S | 401819 | Scaled Integer Format (10000 = 100%)
19 | 6 | Molar Analysis - H2 | 401820 | Scaled Integer Format (10000 = 100%)
20 | 6 | Molar Analysis - CO | 401821 | Scaled Integer Format (10000 = 100%)
21 | 6 | Molar Analysis - O2 | 401822 | Scaled Integer Format (10000 = 100%)
22 | 6 | Molar Analysis - iC4 | 401823 | Scaled Integer Format (10000 = 100%)
23 | 6 | Molar Analysis - C4 | 401824 | Scaled Integer Format (10000 = 100%)
24 | 6 | Molar Analysis - iC5 | 401825 | Scaled Integer Format (10000 = 100%)
25 | 6 | Molar Analysis - C5 | 401826 | Scaled Integer Format (10000 = 100%)
26 | 6 | Molar Analysis - C6 | 401827 | Scaled Integer Format (10000 = 100%)
27 | 6 | Molar Analysis - C7 | 401828 | Scaled Integer Format (10000 = 100%)
28 | 6 | Molar Analysis - C8 | 401829 | Scaled Integer Format (10000 = 100%)
29 | 6 | Molar Analysis - C9 | 401830 | Scaled Integer Format (10000 = 100%)
30 | 6 | Molar Analysis - C10 | 401831 | Scaled Integer Format (10000 = 100%)
31 | 6 | Molar Analysis - He | 401832 | Scaled Integer Format (10000 = 100%)
32 | 6 | Molar Analysis - Ar | 401833 | Scaled Integer Format (10000 = 100%)
33 | 6 | Molar Analysis - C5 (neo-p) | 401834 | Scaled Integer Format (10000 = 100%)
34 | 6 | Molar Analysis - Ux | 401835 | Scaled Integer Format (10000 = 100%)
35 | 6 | Molar Analysis - Uy | 401836 | Scaled Integer Format (10000 = 100%)
36 | 6 | Meter Signals - Reserved | 401837
37 | 6 | Meter Signals - Reserved | 401838
38 | 6 | Meter Signals - Reserved | 401839
39 | 6 | Meter Signals - Reserved | 401840
40 | 6 | Meter Signals - Reset Acc 1 | 401841
41 | 6 | Meter Signals - Reset Acc 2 | 401842
42 | 6 | Meter Signals - Reset Acc 3 | 401843
43 | 6 | Meter Signals - Reset Acc 4 | 401844
44 | 6 | Write Daily Archive | 401845
45 | 6 | Write Hourly Archive | 401846
46 | 6 | Meter Signals - Reserved | 401847
47 | 6 | Meter Signals - Reserved | 401848
48 | 6 | Meter Signals - Reserved | 401849
49 | 6 | Meter Signals - Reserved | 401850
50 | 6 | Meter Signals - Reserved | 401851
51 | 6 | Meter Signals - Reserved | 401852
52 | 6 | Analysis is Present | 401853
53 | 6 | Meter Archive Record Fetch | 401854 | (=0 signal not present)
54 | 6 | Meter Archive Record Age | 401855 | (=0 current)
55 | 6 | Meter Archive File Select | 401856 | (=0 daily, 1=hourly)
Meter 7 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Meter Disable | 402001
1 | 7 | Reserved | 402002
2 | 7 | Temperature | 402003 | Floating Point Format
3 | 7 | Temperature | 402004 | Floating Point Format
4 | 7 | Pressure | 402005 | Floating Point Format
5 | 7 | Pressure | 402006 | Floating Point Format
6 | 7 | Differential Pressure | 402007 | Floating Point Format
7 | 7 | Differential Pressure | 402008 | Floating Point Format
8 | 7 | Reserved | 402009
9 | 7 | Reserved | 402010
10 | 7 | Reserved | 402011
11 | 7 | Reserved | 402012
12 | 7 | Molar Analysis - C1 | 402013 | Scaled Integer Format (10000 = 100%)
13 | 7 | Molar Analysis - N2 | 402014 | Scaled Integer Format (10000 = 100%)
14 | 7 | Molar Analysis - CO2 | 402015 | Scaled Integer Format (10000 = 100%)
15 | 7 | Molar Analysis - C2 | 402016 | Scaled Integer Format (10000 = 100%)
16 | 7 | Molar Analysis - C3 | 402017 | Scaled Integer Format (10000 = 100%)
17 | 7 | Molar Analysis - H2O | 402018 | Scaled Integer Format (10000 = 100%)
18 | 7 | Molar Analysis - H2S | 402019 | Scaled Integer Format (10000 = 100%)
19 | 7 | Molar Analysis - H2 | 402020 | Scaled Integer Format (10000 = 100%)
20 | 7 | Molar Analysis - CO | 402021 | Scaled Integer Format (10000 = 100%)
21 | 7 | Molar Analysis - O2 | 402022 | Scaled Integer Format (10000 = 100%)
22 | 7 | Molar Analysis - iC4 | 402023 | Scaled Integer Format (10000 = 100%)
23 | 7 | Molar Analysis - C4 | 402024 | Scaled Integer Format (10000 = 100%)
24 | 7 | Molar Analysis - iC5 | 402025 | Scaled Integer Format (10000 = 100%)
25 | 7 | Molar Analysis - C5 | 402026 | Scaled Integer Format (10000 = 100%)
26 | 7 | Molar Analysis - C6 | 402027 | Scaled Integer Format (10000 = 100%)
27 | 7 | Molar Analysis - C7 | 402028 | Scaled Integer Format (10000 = 100%)
28 | 7 | Molar Analysis - C8 | 402029 | Scaled Integer Format (10000 = 100%)
29 | 7 | Molar Analysis - C9 | 402030 | Scaled Integer Format (10000 = 100%)
30 | 7 | Molar Analysis - C10 | 402031 | Scaled Integer Format (10000 = 100%)
31 | 7 | Molar Analysis - He | 402032 | Scaled Integer Format (10000 = 100%)
32 | 7 | Molar Analysis - Ar | 402033 | Scaled Integer Format (10000 = 100%)
33 | 7 | Molar Analysis - C5 (neo-p) | 402034 | Scaled Integer Format (10000 = 100%)
34 | 7 | Molar Analysis - Ux | 402035 | Scaled Integer Format (10000 = 100%)
35 | 7 | Molar Analysis - Uy | 402036 | Scaled Integer Format (10000 = 100%)
36 | 7 | Meter Signals - Reserved | 402037
37 | 7 | Meter Signals - Reserved | 402038
38 | 7 | Meter Signals - Reserved | 402039
39 | 7 | Meter Signals - Reserved | 402040
40 | 7 | Meter Signals - Reset Acc 1 | 402041
41 | 7 | Meter Signals - Reset Acc 2 | 402042
42 | 7 | Meter Signals - Reset Acc 3 | 402043
43 | 7 | Meter Signals - Reset Acc 4 | 402044
44 | 7 | Write Daily Archive | 402045
45 | 7 | Write Hourly Archive | 402046
46 | 7 | Meter Signals - Reserved | 402047
47 | 7 | Meter Signals - Reserved | 402048
48 | 7 | Meter Signals - Reserved | 402049
49 | 7 | Meter Signals - Reserved | 402050
50 | 7 | Meter Signals - Reserved | 402051
51 | 7 | Meter Signals - Reserved | 402052
52 | 7 | Analysis is Present | 402053
53 | 7 | Meter Archive Record Fetch | 402054 | (=0 signal not present)
54 | 7 | Meter Archive Record Age | 402055 | (=0 current)
55 | 7 | Meter Archive File Select | 402056 | (=0 daily, 1=hourly)
Meter 8 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Meter Disable | 402201
1 | 8 | Reserved | 402202
2 | 8 | Temperature | 402203 | Floating Point Format
3 | 8 | Temperature | 402204 | Floating Point Format
4 | 8 | Pressure | 402205 | Floating Point Format
5 | 8 | Pressure | 402206 | Floating Point Format
6 | 8 | Differential Pressure | 402207 | Floating Point Format
7 | 8 | Differential Pressure | 402208 | Floating Point Format
8 | 8 | Reserved | 402209
9 | 8 | Reserved | 402210
10 | 8 | Reserved | 402211
11 | 8 | Reserved | 402212
12 | 8 | Molar Analysis - C1 | 402213 | Scaled Integer Format (10000 = 100%)
13 | 8 | Molar Analysis - N2 | 402214 | Scaled Integer Format (10000 = 100%)
14 | 8 | Molar Analysis - CO2 | 402215 | Scaled Integer Format (10000 = 100%)
15 | 8 | Molar Analysis - C2 | 402216 | Scaled Integer Format (10000 = 100%)
16 | 8 | Molar Analysis - C3 | 402217 | Scaled Integer Format (10000 = 100%)
17 | 8 | Molar Analysis - H2O | 402218 | Scaled Integer Format (10000 = 100%)
18 | 8 | Molar Analysis - H2S | 402219 | Scaled Integer Format (10000 = 100%)
19 | 8 | Molar Analysis - H2 | 402220 | Scaled Integer Format (10000 = 100%)
20 | 8 | Molar Analysis - CO | 402221 | Scaled Integer Format (10000 = 100%)
21 | 8 | Molar Analysis - O2 | 402222 | Scaled Integer Format (10000 = 100%)
22 | 8 | Molar Analysis - iC4 | 402223 | Scaled Integer Format (10000 = 100%)
23 | 8 | Molar Analysis - C4 | 402224 | Scaled Integer Format (10000 = 100%)
24 | 8 | Molar Analysis - iC5 | 402225 | Scaled Integer Format (10000 = 100%)
25 | 8 | Molar Analysis - C5 | 402226 | Scaled Integer Format (10000 = 100%)
26 | 8 | Molar Analysis - C6 | 402227 | Scaled Integer Format (10000 = 100%)
27 | 8 | Molar Analysis - C7 | 402228 | Scaled Integer Format (10000 = 100%)
28 | 8 | Molar Analysis - C8 | 402229 | Scaled Integer Format (10000 = 100%)
29 | 8 | Molar Analysis - C9 | 402230 | Scaled Integer Format (10000 = 100%)
30 | 8 | Molar Analysis - C10 | 402231 | Scaled Integer Format (10000 = 100%)
31 | 8 | Molar Analysis - He | 402232 | Scaled Integer Format (10000 = 100%)
32 | 8 | Molar Analysis - Ar | 402233 | Scaled Integer Format (10000 = 100%)
33 | 8 | Molar Analysis - C5 (neo-p) | 402234 | Scaled Integer Format (10000 = 100%)
34 | 8 | Molar Analysis - Ux | 402235 | Scaled Integer Format (10000 = 100%)
35 | 8 | Molar Analysis - Uy | 402236 | Scaled Integer Format (10000 = 100%)
36 | 8 | Meter Signals - Reserved | 402237
37 | 8 | Meter Signals - Reserved | 402238
38 | 8 | Meter Signals - Reserved | 402239
39 | 8 | Meter Signals - Reserved | 402240
40 | 8 | Meter Signals - Reset Acc 1 | 402241
41 | 8 | Meter Signals - Reset Acc 2 | 402242
42 | 8 | Meter Signals - Reset Acc 3 | 402243
43 | 8 | Meter Signals - Reset Acc 4 | 402244
44 | 8 | Write Daily Archive | 402245
45 | 8 | Write Hourly Archive | 402246
46 | 8 | Meter Signals - Reserved | 402247
47 | 8 | Meter Signals - Reserved | 402248
48 | 8 | Meter Signals - Reserved | 402249
49 | 8 | Meter Signals - Reserved | 402250
50 | 8 | Meter Signals - Reserved | 402251
51 | 8 | Meter Signals - Reserved | 402252
52 | 8 | Analysis is Present | 402253
53 | 8 | Meter Archive Record Fetch | 402254 | (=0 signal not present)
54 | 8 | Meter Archive Record Age | 402255 | (=0 current)
55 | 8 | Meter Archive File Select | 402256 | (=0 daily, 1=hourly)
Meter 9 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Meter Disable | 402401
1 | 9 | Reserved | 402402
2 | 9 | Temperature | 402403 | Floating Point Format
3 | 9 | Temperature | 402404 | Floating Point Format
4 | 9 | Pressure | 402405 | Floating Point Format
5 | 9 | Pressure | 402406 | Floating Point Format
6 | 9 | Differential Pressure | 402407 | Floating Point Format
7 | 9 | Differential Pressure | 402408 | Floating Point Format
8 | 9 | Reserved | 402409
9 | 9 | Reserved | 402410
10 | 9 | Reserved | 402411
11 | 9 | Reserved | 402412
12 | 9 | Molar Analysis - C1 | 402413 | Scaled Integer Format (10000 = 100%)
13 | 9 | Molar Analysis - N2 | 402414 | Scaled Integer Format (10000 = 100%)
14 | 9 | Molar Analysis - CO2 | 402415 | Scaled Integer Format (10000 = 100%)
15 | 9 | Molar Analysis - C2 | 402416 | Scaled Integer Format (10000 = 100%)
16 | 9 | Molar Analysis - C3 | 402417 | Scaled Integer Format (10000 = 100%)
17 | 9 | Molar Analysis - H2O | 402418 | Scaled Integer Format (10000 = 100%)
18 | 9 | Molar Analysis - H2S | 402419 | Scaled Integer Format (10000 = 100%)
19 | 9 | Molar Analysis - H2 | 402420 | Scaled Integer Format (10000 = 100%)
20 | 9 | Molar Analysis - CO | 402421 | Scaled Integer Format (10000 = 100%)
21 | 9 | Molar Analysis - O2 | 402422 | Scaled Integer Format (10000 = 100%)
22 | 9 | Molar Analysis - iC4 | 402423 | Scaled Integer Format (10000 = 100%)
23 | 9 | Molar Analysis - C4 | 402424 | Scaled Integer Format (10000 = 100%)
24 | 9 | Molar Analysis - iC5 | 402425 | Scaled Integer Format (10000 = 100%)
25 | 9 | Molar Analysis - C5 | 402426 | Scaled Integer Format (10000 = 100%)
26 | 9 | Molar Analysis - C6 | 402427 | Scaled Integer Format (10000 = 100%)
27 | 9 | Molar Analysis - C7 | 402428 | Scaled Integer Format (10000 = 100%)
28 | 9 | Molar Analysis - C8 | 402429 | Scaled Integer Format (10000 = 100%)
29 | 9 | Molar Analysis - C9 | 402430 | Scaled Integer Format (10000 = 100%)
30 | 9 | Molar Analysis - C10 | 402431 | Scaled Integer Format (10000 = 100%)
31 | 9 | Molar Analysis - He | 402432 | Scaled Integer Format (10000 = 100%)
32 | 9 | Molar Analysis - Ar | 402433 | Scaled Integer Format (10000 = 100%)
33 | 9 | Molar Analysis - C5 (neo-p) | 402434 | Scaled Integer Format (10000 = 100%)
34 | 9 | Molar Analysis - Ux | 402435 | Scaled Integer Format (10000 = 100%)
35 | 9 | Molar Analysis - Uy | 402436 | Scaled Integer Format (10000 = 100%)
36 | 9 | Meter Signals - Reserved | 402437
37 | 9 | Meter Signals - Reserved | 402438
38 | 9 | Meter Signals - Reserved | 402439
39 | 9 | Meter Signals - Reserved | 402440
40 | 9 | Meter Signals - Reset Acc 1 | 402441
41 | 9 | Meter Signals - Reset Acc 2 | 402442
42 | 9 | Meter Signals - Reset Acc 3 | 402443
43 | 9 | Meter Signals - Reset Acc 4 | 402444
44 | 9 | Write Daily Archive | 402445
45 | 9 | Write Hourly Archive | 402446
46 | 9 | Meter Signals - Reserved | 402447
47 | 9 | Meter Signals - Reserved | 402448
48 | 9 | Meter Signals - Reserved | 402449
49 | 9 | Meter Signals - Reserved | 402450
50 | 9 | Meter Signals - Reserved | 402451
51 | 9 | Meter Signals - Reserved | 402452
52 | 9 | Analysis is Present | 402453
53 | 9 | Meter Archive Record Fetch | 402454 | (=0 signal not present)
54 | 9 | Meter Archive Record Age | 402455 | (=0 current)
55 | 9 | Meter Archive File Select | 402456 | (=0 daily, 1=hourly)
Meter 10 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Meter Disable | 402601
1 | 10 | Reserved | 402602
2 | 10 | Temperature | 402603 | Floating Point Format
3 | 10 | Temperature | 402604 | Floating Point Format
4 | 10 | Pressure | 402605 | Floating Point Format
5 | 10 | Pressure | 402606 | Floating Point Format
6 | 10 | Differential Pressure | 402607 | Floating Point Format
7 | 10 | Differential Pressure | 402608 | Floating Point Format
8 | 10 | Reserved | 402609
9 | 10 | Reserved | 402610
10 | 10 | Reserved | 402611
11 | 10 | Reserved | 402612
12 | 10 | Molar Analysis - C1 | 402613 | Scaled Integer Format (10000 = 100%)
13 | 10 | Molar Analysis - N2 | 402614 | Scaled Integer Format (10000 = 100%)
14 | 10 | Molar Analysis - CO2 | 402615 | Scaled Integer Format (10000 = 100%)
15 | 10 | Molar Analysis - C2 | 402616 | Scaled Integer Format (10000 = 100%)
16 | 10 | Molar Analysis - C3 | 402617 | Scaled Integer Format (10000 = 100%)
17 | 10 | Molar Analysis - H2O | 402618 | Scaled Integer Format (10000 = 100%)
18 | 10 | Molar Analysis - H2S | 402619 | Scaled Integer Format (10000 = 100%)
19 | 10 | Molar Analysis - H2 | 402620 | Scaled Integer Format (10000 = 100%)
20 | 10 | Molar Analysis - CO | 402621 | Scaled Integer Format (10000 = 100%)
21 | 10 | Molar Analysis - O2 | 402622 | Scaled Integer Format (10000 = 100%)
22 | 10 | Molar Analysis - iC4 | 402623 | Scaled Integer Format (10000 = 100%)
23 | 10 | Molar Analysis - C4 | 402624 | Scaled Integer Format (10000 = 100%)
24 | 10 | Molar Analysis - iC5 | 402625 | Scaled Integer Format (10000 = 100%)
25 | 10 | Molar Analysis - C5 | 402626 | Scaled Integer Format (10000 = 100%)
26 | 10 | Molar Analysis - C6 | 402627 | Scaled Integer Format (10000 = 100%)
27 | 10 | Molar Analysis - C7 | 402628 | Scaled Integer Format (10000 = 100%)
28 | 10 | Molar Analysis - C8 | 402629 | Scaled Integer Format (10000 = 100%)
29 | 10 | Molar Analysis - C9 | 402630 | Scaled Integer Format (10000 = 100%)
30 | 10 | Molar Analysis - C10 | 402631 | Scaled Integer Format (10000 = 100%)
31 | 10 | Molar Analysis - He | 402632 | Scaled Integer Format (10000 = 100%)
32 | 10 | Molar Analysis - Ar | 402633 | Scaled Integer Format (10000 = 100%)
33 | 10 | Molar Analysis - C5 (neo-p) | 402634 | Scaled Integer Format (10000 = 100%)
34 | 10 | Molar Analysis - Ux | 402635 | Scaled Integer Format (10000 = 100%)
35 | 10 | Molar Analysis - Uy | 402636 | Scaled Integer Format (10000 = 100%)
36 | 10 | Meter Signals - Reserved | 402637
37 | 10 | Meter Signals - Reserved | 402638
38 | 10 | Meter Signals - Reserved | 402639
39 | 10 | Meter Signals - Reserved | 402640
40 | 10 | Meter Signals - Reset Acc 1 | 402641
41 | 10 | Meter Signals - Reset Acc 2 | 402642
42 | 10 | Meter Signals - Reset Acc 3 | 402643
43 | 10 | Meter Signals - Reset Acc 4 | 402644
44 | 10 | Write Daily Archive | 402645
45 | 10 | Write Hourly Archive | 402646
46 | 10 | Meter Signals - Reserved | 402647
47 | 10 | Meter Signals - Reserved | 402648
48 | 10 | Meter Signals - Reserved | 402649
49 | 10 | Meter Signals - Reserved | 402650
50 | 10 | Meter Signals - Reserved | 402651
51 | 10 | Meter Signals - Reserved | 402652
52 | 10 | Analysis is Present | 402653
53 | 10 | Meter Archive Record Fetch | 402654 | (=0 signal not present)
54 | 10 | Meter Archive Record Age | 402655 | (=0 current)
55 | 10 | Meter Archive File Select | 402656 | (=0 daily, 1=hourly)
Meter 11 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Meter Disable | 402801
1 | 11 | Reserved | 402802
2 | 11 | Temperature | 402803 | Floating Point Format
3 | 11 | Temperature | 402804 | Floating Point Format
4 | 11 | Pressure | 402805 | Floating Point Format
5 | 11 | Pressure | 402806 | Floating Point Format
6 | 11 | Differential Pressure | 402807 | Floating Point Format
7 | 11 | Differential Pressure | 402808 | Floating Point Format
8 | 11 | Reserved | 402809
9 | 11 | Reserved | 402810
10 | 11 | Reserved | 402811
11 | 11 | Reserved | 402812
12 | 11 | Molar Analysis - C1 | 402813 | Scaled Integer Format (10000 = 100%)
13 | 11 | Molar Analysis - N2 | 402814 | Scaled Integer Format (10000 = 100%)
14 | 11 | Molar Analysis - CO2 | 402815 | Scaled Integer Format (10000 = 100%)
15 | 11 | Molar Analysis - C2 | 402816 | Scaled Integer Format (10000 = 100%)
16 | 11 | Molar Analysis - C3 | 402817 | Scaled Integer Format (10000 = 100%)
17 | 11 | Molar Analysis - H2O | 402818 | Scaled Integer Format (10000 = 100%)
18 | 11 | Molar Analysis - H2S | 402819 | Scaled Integer Format (10000 = 100%)
19 | 11 | Molar Analysis - H2 | 402820 | Scaled Integer Format (10000 = 100%)
20 | 11 | Molar Analysis - CO | 402821 | Scaled Integer Format (10000 = 100%)
21 | 11 | Molar Analysis - O2 | 402822 | Scaled Integer Format (10000 = 100%)
22 | 11 | Molar Analysis - iC4 | 402823 | Scaled Integer Format (10000 = 100%)
23 | 11 | Molar Analysis - C4 | 402824 | Scaled Integer Format (10000 = 100%)
24 | 11 | Molar Analysis - iC5 | 402825 | Scaled Integer Format (10000 = 100%)
25 | 11 | Molar Analysis - C5 | 402826 | Scaled Integer Format (10000 = 100%)
26 | 11 | Molar Analysis - C6 | 402827 | Scaled Integer Format (10000 = 100%)
27 | 11 | Molar Analysis - C7 | 402828 | Scaled Integer Format (10000 = 100%)
28 | 11 | Molar Analysis - C8 | 402829 | Scaled Integer Format (10000 = 100%)
29 | 11 | Molar Analysis - C9 | 402830 | Scaled Integer Format (10000 = 100%)
30 | 11 | Molar Analysis - C10 | 402831 | Scaled Integer Format (10000 = 100%)
31 | 11 | Molar Analysis - He | 402832 | Scaled Integer Format (10000 = 100%)
32 | 11 | Molar Analysis - Ar | 402833 | Scaled Integer Format (10000 = 100%)
33 | 11 | Molar Analysis - C5 (neo-p) | 402834 | Scaled Integer Format (10000 = 100%)
34 | 11 | Molar Analysis - Ux | 402835 | Scaled Integer Format (10000 = 100%)
35 | 11 | Molar Analysis - Uy | 402836 | Scaled Integer Format (10000 = 100%)
36 | 11 | Meter Signals - Reserved | 402837
37 | 11 | Meter Signals - Reserved | 402838
38 | 11 | Meter Signals - Reserved | 402839
39 | 11 | Meter Signals - Reserved | 402840
40 | 11 | Meter Signals - Reset Acc 1 | 402841
41 | 11 | Meter Signals - Reset Acc 2 | 402842
42 | 11 | Meter Signals - Reset Acc 3 | 402843
43 | 11 | Meter Signals - Reset Acc 4 | 402844
44 | 11 | Write Daily Archive | 402845
45 | 11 | Write Hourly Archive | 402846
46 | 11 | Meter Signals - Reserved | 402847
47 | 11 | Meter Signals - Reserved | 402848
48 | 11 | Meter Signals - Reserved | 402849
49 | 11 | Meter Signals - Reserved | 402850
50 | 11 | Meter Signals - Reserved | 402851
51 | 11 | Meter Signals - Reserved | 402852
52 | 11 | Analysis is Present | 402853
53 | 11 | Meter Archive Record Fetch | 402854 | (=0 signal not present)
54 | 11 | Meter Archive Record Age | 402855 | (=0 current)
55 | 11 | Meter Archive File Select | 402856 | (=0 daily, 1=hourly)
Meter 12 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Meter Disable | 403001
1 | 12 | Reserved | 403002
2 | 12 | Temperature | 403003 | Floating Point Format
3 | 12 | Temperature | 403004 | Floating Point Format
4 | 12 | Pressure | 403005 | Floating Point Format
5 | 12 | Pressure | 403006 | Floating Point Format
6 | 12 | Differential Pressure | 403007 | Floating Point Format
7 | 12 | Differential Pressure | 403008 | Floating Point Format
8 | 12 | Reserved | 403009
9 | 12 | Reserved | 403010
10 | 12 | Reserved | 403011
11 | 12 | Reserved | 403012
12 | 12 | Molar Analysis - C1 | 403013 | Scaled Integer Format (10000 = 100%)
13 | 12 | Molar Analysis - N2 | 403014 | Scaled Integer Format (10000 = 100%)
14 | 12 | Molar Analysis - CO2 | 403015 | Scaled Integer Format (10000 = 100%)
15 | 12 | Molar Analysis - C2 | 403016 | Scaled Integer Format (10000 = 100%)
16 | 12 | Molar Analysis - C3 | 403017 | Scaled Integer Format (10000 = 100%)
17 | 12 | Molar Analysis - H2O | 403018 | Scaled Integer Format (10000 = 100%)
18 | 12 | Molar Analysis - H2S | 403019 | Scaled Integer Format (10000 = 100%)
19 | 12 | Molar Analysis - H2 | 403020 | Scaled Integer Format (10000 = 100%)
20 | 12 | Molar Analysis - CO | 403021 | Scaled Integer Format (10000 = 100%)
21 | 12 | Molar Analysis - O2 | 403022 | Scaled Integer Format (10000 = 100%)
22 | 12 | Molar Analysis - iC4 | 403023 | Scaled Integer Format (10000 = 100%)
23 | 12 | Molar Analysis - C4 | 403024 | Scaled Integer Format (10000 = 100%)
24 | 12 | Molar Analysis - iC5 | 403025 | Scaled Integer Format (10000 = 100%)
25 | 12 | Molar Analysis - C5 | 403026 | Scaled Integer Format (10000 = 100%)
26 | 12 | Molar Analysis - C6 | 403027 | Scaled Integer Format (10000 = 100%)
27 | 12 | Molar Analysis - C7 | 403028 | Scaled Integer Format (10000 = 100%)
28 | 12 | Molar Analysis - C8 | 403029 | Scaled Integer Format (10000 = 100%)
29 | 12 | Molar Analysis - C9 | 403030 | Scaled Integer Format (10000 = 100%)
30 | 12 | Molar Analysis - C10 | 403031 | Scaled Integer Format (10000 = 100%)
31 | 12 | Molar Analysis - He | 403032 | Scaled Integer Format (10000 = 100%)
32 | 12 | Molar Analysis - Ar | 403033 | Scaled Integer Format (10000 = 100%)
33 | 12 | Molar Analysis - C5 (neo-p) | 403034 | Scaled Integer Format (10000 = 100%)
34 | 12 | Molar Analysis - Ux | 403035 | Scaled Integer Format (10000 = 100%)
35 | 12 | Molar Analysis - Uy | 403036 | Scaled Integer Format (10000 = 100%)
36 | 12 | Meter Signals - Reserved | 403037
37 | 12 | Meter Signals - Reserved | 403038
38 | 12 | Meter Signals - Reserved | 403039
39 | 12 | Meter Signals - Reserved | 403040
40 | 12 | Meter Signals - Reset Acc 1 | 403041
41 | 12 | Meter Signals - Reset Acc 2 | 403042
42 | 12 | Meter Signals - Reset Acc 3 | 403043
43 | 12 | Meter Signals - Reset Acc 4 | 403044
44 | 12 | Write Daily Archive | 403045
45 | 12 | Write Hourly Archive | 403046
46 | 12 | Meter Signals - Reserved | 403047
47 | 12 | Meter Signals - Reserved | 403048
48 | 12 | Meter Signals - Reserved | 403049
49 | 12 | Meter Signals - Reserved | 403050
50 | 12 | Meter Signals - Reserved | 403051
51 | 12 | Meter Signals - Reserved | 403052
52 | 12 | Analysis is Present | 403053
53 | 12 | Meter Archive Record Fetch | 403054 | (=0 signal not present)
54 | 12 | Meter Archive Record Age | 403055 | (=0 current)
55 | 12 | Meter Archive File Select | 403056 | (=0 daily, 1=hourly)
Meter 13 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Meter Disable | 403201
1 | 13 | Reserved | 403202
2 | 13 | Temperature | 403203 | Floating Point Format
3 | 13 | Temperature | 403204 | Floating Point Format
4 | 13 | Pressure | 403205 | Floating Point Format
5 | 13 | Pressure | 403206 | Floating Point Format
6 | 13 | Differential Pressure | 403207 | Floating Point Format
7 | 13 | Differential Pressure | 403208 | Floating Point Format
8 | 13 | Reserved | 403209
9 | 13 | Reserved | 403210
10 | 13 | Reserved | 403211
11 | 13 | Reserved | 403212
12 | 13 | Molar Analysis - C1 | 403213 | Scaled Integer Format (10000 = 100%)
13 | 13 | Molar Analysis - N2 | 403214 | Scaled Integer Format (10000 = 100%)
14 | 13 | Molar Analysis - CO2 | 403215 | Scaled Integer Format (10000 = 100%)
15 | 13 | Molar Analysis - C2 | 403216 | Scaled Integer Format (10000 = 100%)
16 | 13 | Molar Analysis - C3 | 403217 | Scaled Integer Format (10000 = 100%)
17 | 13 | Molar Analysis - H2O | 403218 | Scaled Integer Format (10000 = 100%)
18 | 13 | Molar Analysis - H2S | 403219 | Scaled Integer Format (10000 = 100%)
19 | 13 | Molar Analysis - H2 | 403220 | Scaled Integer Format (10000 = 100%)
20 | 13 | Molar Analysis - CO | 403221 | Scaled Integer Format (10000 = 100%)
21 | 13 | Molar Analysis - O2 | 403222 | Scaled Integer Format (10000 = 100%)
22 | 13 | Molar Analysis - iC4 | 403223 | Scaled Integer Format (10000 = 100%)
23 | 13 | Molar Analysis - C4 | 403224 | Scaled Integer Format (10000 = 100%)
24 | 13 | Molar Analysis - iC5 | 403225 | Scaled Integer Format (10000 = 100%)
25 | 13 | Molar Analysis - C5 | 403226 | Scaled Integer Format (10000 = 100%)
26 | 13 | Molar Analysis - C6 | 403227 | Scaled Integer Format (10000 = 100%)
27 | 13 | Molar Analysis - C7 | 403228 | Scaled Integer Format (10000 = 100%)
28 | 13 | Molar Analysis - C8 | 403229 | Scaled Integer Format (10000 = 100%)
29 | 13 | Molar Analysis - C9 | 403230 | Scaled Integer Format (10000 = 100%)
30 | 13 | Molar Analysis - C10 | 403231 | Scaled Integer Format (10000 = 100%)
31 | 13 | Molar Analysis - He | 403232 | Scaled Integer Format (10000 = 100%)
32 | 13 | Molar Analysis - Ar | 403233 | Scaled Integer Format (10000 = 100%)
33 | 13 | Molar Analysis - C5 (neo-p) | 403234 | Scaled Integer Format (10000 = 100%)
34 | 13 | Molar Analysis - Ux | 403235 | Scaled Integer Format (10000 = 100%)
35 | 13 | Molar Analysis - Uy | 403236 | Scaled Integer Format (10000 = 100%)
36 | 13 | Meter Signals - Reserved | 403237
37 | 13 | Meter Signals - Reserved | 403238
38 | 13 | Meter Signals - Reserved | 403239
39 | 13 | Meter Signals - Reserved | 403240
40 | 13 | Meter Signals - Reset Acc 1 | 403241
41 | 13 | Meter Signals - Reset Acc 2 | 403242
42 | 13 | Meter Signals - Reset Acc 3 | 403243
43 | 13 | Meter Signals - Reset Acc 4 | 403244
44 | 13 | Write Daily Archive | 403245
45 | 13 | Write Hourly Archive | 403246
46 | 13 | Meter Signals - Reserved | 403247
47 | 13 | Meter Signals - Reserved | 403248
48 | 13 | Meter Signals - Reserved | 403249
49 | 13 | Meter Signals - Reserved | 403250
50 | 13 | Meter Signals - Reserved | 403251
51 | 13 | Meter Signals - Reserved | 403252
52 | 13 | Analysis is Present | 403253
53 | 13 | Meter Archive Record Fetch | 403254 | (=0 signal not present)
54 | 13 | Meter Archive Record Age | 403255 | (=0 current)
55 | 13 | Meter Archive File Select | 403256 | (=0 daily, 1=hourly)
Meter 14 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Meter Disable | 403401
1 | 14 | Reserved | 403402
2 | 14 | Temperature | 403403 | Floating Point Format
3 | 14 | Temperature | 403404 | Floating Point Format
4 | 14 | Pressure | 403405 | Floating Point Format
5 | 14 | Pressure | 403406 | Floating Point Format
6 | 14 | Differential Pressure | 403407 | Floating Point Format
7 | 14 | Differential Pressure | 403408 | Floating Point Format
8 | 14 | Reserved | 403409
9 | 14 | Reserved | 403410
10 | 14 | Reserved | 403411
11 | 14 | Reserved | 403412
12 | 14 | Molar Analysis - C1 | 403413 | Scaled Integer Format (10000 = 100%)
13 | 14 | Molar Analysis - N2 | 403414 | Scaled Integer Format (10000 = 100%)
14 | 14 | Molar Analysis - CO2 | 403415 | Scaled Integer Format (10000 = 100%)
15 | 14 | Molar Analysis - C2 | 403416 | Scaled Integer Format (10000 = 100%)
16 | 14 | Molar Analysis - C3 | 403417 | Scaled Integer Format (10000 = 100%)
17 | 14 | Molar Analysis - H2O | 403418 | Scaled Integer Format (10000 = 100%)
18 | 14 | Molar Analysis - H2S | 403419 | Scaled Integer Format (10000 = 100%)
19 | 14 | Molar Analysis - H2 | 403420 | Scaled Integer Format (10000 = 100%)
20 | 14 | Molar Analysis - CO | 403421 | Scaled Integer Format (10000 = 100%)
21 | 14 | Molar Analysis - O2 | 403422 | Scaled Integer Format (10000 = 100%)
22 | 14 | Molar Analysis - iC4 | 403423 | Scaled Integer Format (10000 = 100%)
23 | 14 | Molar Analysis - C4 | 403424 | Scaled Integer Format (10000 = 100%)
24 | 14 | Molar Analysis - iC5 | 403425 | Scaled Integer Format (10000 = 100%)
25 | 14 | Molar Analysis - C5 | 403426 | Scaled Integer Format (10000 = 100%)
26 | 14 | Molar Analysis - C6 | 403427 | Scaled Integer Format (10000 = 100%)
27 | 14 | Molar Analysis - C7 | 403428 | Scaled Integer Format (10000 = 100%)
28 | 14 | Molar Analysis - C8 | 403429 | Scaled Integer Format (10000 = 100%)
29 | 14 | Molar Analysis - C9 | 403430 | Scaled Integer Format (10000 = 100%)
30 | 14 | Molar Analysis - C10 | 403431 | Scaled Integer Format (10000 = 100%)
31 | 14 | Molar Analysis - He | 403432 | Scaled Integer Format (10000 = 100%)
32 | 14 | Molar Analysis - Ar | 403433 | Scaled Integer Format (10000 = 100%)
33 | 14 | Molar Analysis - C5 (neo-p) | 403434 | Scaled Integer Format (10000 = 100%)
34 | 14 | Molar Analysis - Ux | 403435 | Scaled Integer Format (10000 = 100%)
35 | 14 | Molar Analysis - Uy | 403436 | Scaled Integer Format (10000 = 100%)
36 | 14 | Meter Signals - Reserved | 403437
37 | 14 | Meter Signals - Reserved | 403438
38 | 14 | Meter Signals - Reserved | 403439
39 | 14 | Meter Signals - Reserved | 403440
40 | 14 | Meter Signals - Reset Acc 1 | 403441
41 | 14 | Meter Signals - Reset Acc 2 | 403442
42 | 14 | Meter Signals - Reset Acc 3 | 403443
43 | 14 | Meter Signals - Reset Acc 4 | 403444
44 | 14 | Write Daily Archive | 403445
45 | 14 | Write Hourly Archive | 403446
46 | 14 | Meter Signals - Reserved | 403447
47 | 14 | Meter Signals - Reserved | 403448
48 | 14 | Meter Signals - Reserved | 403449
49 | 14 | Meter Signals - Reserved | 403450
50 | 14 | Meter Signals - Reserved | 403451
51 | 14 | Meter Signals - Reserved | 403452
52 | 14 | Analysis is Present | 403453
53 | 14 | Meter Archive Record Fetch | 403454 | (=0 signal not present)
54 | 14 | Meter Archive Record Age | 403455 | (=0 current)
55 | 14 | Meter Archive File Select | 403456 | (=0 daily, 1=hourly)
Meter 15 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Meter Disable | 403601
1 | 15 | Reserved | 403602
2 | 15 | Temperature | 403603 | Floating Point Format
3 | 15 | Temperature | 403604 | Floating Point Format
4 | 15 | Pressure | 403605 | Floating Point Format
5 | 15 | Pressure | 403606 | Floating Point Format
6 | 15 | Differential Pressure | 403607 | Floating Point Format
7 | 15 | Differential Pressure | 403608 | Floating Point Format
8 | 15 | Reserved | 403609
9 | 15 | Reserved | 403610
10 | 15 | Reserved | 403611
11 | 15 | Reserved | 403612
12 | 15 | Molar Analysis - C1 | 403613 | Scaled Integer Format (10000 = 100%)
13 | 15 | Molar Analysis - N2 | 403614 | Scaled Integer Format (10000 = 100%)
14 | 15 | Molar Analysis - CO2 | 403615 | Scaled Integer Format (10000 = 100%)
15 | 15 | Molar Analysis - C2 | 403616 | Scaled Integer Format (10000 = 100%)
16 | 15 | Molar Analysis - C3 | 403617 | Scaled Integer Format (10000 = 100%)
17 | 15 | Molar Analysis - H2O | 403618 | Scaled Integer Format (10000 = 100%)
18 | 15 | Molar Analysis - H2S | 403619 | Scaled Integer Format (10000 = 100%)
19 | 15 | Molar Analysis - H2 | 403620 | Scaled Integer Format (10000 = 100%)
20 | 15 | Molar Analysis - CO | 403621 | Scaled Integer Format (10000 = 100%)
21 | 15 | Molar Analysis - O2 | 403622 | Scaled Integer Format (10000 = 100%)
22 | 15 | Molar Analysis - iC4 | 403623 | Scaled Integer Format (10000 = 100%)
23 | 15 | Molar Analysis - C4 | 403624 | Scaled Integer Format (10000 = 100%)
24 | 15 | Molar Analysis - iC5 | 403625 | Scaled Integer Format (10000 = 100%)
25 | 15 | Molar Analysis - C5 | 403626 | Scaled Integer Format (10000 = 100%)
26 | 15 | Molar Analysis - C6 | 403627 | Scaled Integer Format (10000 = 100%)
27 | 15 | Molar Analysis - C7 | 403628 | Scaled Integer Format (10000 = 100%)
28 | 15 | Molar Analysis - C8 | 403629 | Scaled Integer Format (10000 = 100%)
29 | 15 | Molar Analysis - C9 | 403630 | Scaled Integer Format (10000 = 100%)
30 | 15 | Molar Analysis - C10 | 403631 | Scaled Integer Format (10000 = 100%)
31 | 15 | Molar Analysis - He | 403632 | Scaled Integer Format (10000 = 100%)
32 | 15 | Molar Analysis - Ar | 403633 | Scaled Integer Format (10000 = 100%)
33 | 15 | Molar Analysis - C5 (neo-p) | 403634 | Scaled Integer Format (10000 = 100%)
34 | 15 | Molar Analysis - Ux | 403635 | Scaled Integer Format (10000 = 100%)
35 | 15 | Molar Analysis - Uy | 403636 | Scaled Integer Format (10000 = 100%)
36 | 15 | Meter Signals - Reserved | 403637
37 | 15 | Meter Signals - Reserved | 403638
38 | 15 | Meter Signals - Reserved | 403639
39 | 15 | Meter Signals - Reserved | 403640
40 | 15 | Meter Signals - Reset Acc 1 | 403641
41 | 15 | Meter Signals - Reset Acc 2 | 403642
42 | 15 | Meter Signals - Reset Acc 3 | 403643
43 | 15 | Meter Signals - Reset Acc 4 | 403644
44 | 15 | Write Daily Archive | 403645
45 | 15 | Write Hourly Archive | 403646
46 | 15 | Meter Signals - Reserved | 403647
47 | 15 | Meter Signals - Reserved | 403648
48 | 15 | Meter Signals - Reserved | 403649
49 | 15 | Meter Signals - Reserved | 403650
50 | 15 | Meter Signals - Reserved | 403651
51 | 15 | Meter Signals - Reserved | 403652
52 | 15 | Analysis is Present | 403653
53 | 15 | Meter Archive Record Fetch | 403654 | (=0 signal not present)
54 | 15 | Meter Archive Record Age | 403655 | (=0 current)
55 | 15 | Meter Archive File Select | 403656 | (=0 daily, 1=hourly)
Meter 16 Variables Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Meter Disable | 403801
1 | 16 | Reserved | 403802
2 | 16 | Temperature | 403803 | Floating Point Format
3 | 16 | Temperature | 403804 | Floating Point Format
4 | 16 | Pressure | 403805 | Floating Point Format
5 | 16 | Pressure | 403806 | Floating Point Format
6 | 16 | Differential Pressure | 403807 | Floating Point Format
7 | 16 | Differential Pressure | 403808 | Floating Point Format
8 | 16 | Reserved | 403809
9 | 16 | Reserved | 403810
10 | 16 | Reserved | 403811
11 | 16 | Reserved | 403812
12 | 16 | Molar Analysis - C1 | 403813 | Scaled Integer Format (10000 = 100%)
13 | 16 | Molar Analysis - N2 | 403814 | Scaled Integer Format (10000 = 100%)
14 | 16 | Molar Analysis - CO2 | 403815 | Scaled Integer Format (10000 = 100%)
15 | 16 | Molar Analysis - C2 | 403816 | Scaled Integer Format (10000 = 100%)
16 | 16 | Molar Analysis - C3 | 403817 | Scaled Integer Format (10000 = 100%)
17 | 16 | Molar Analysis - H2O | 403818 | Scaled Integer Format (10000 = 100%)
18 | 16 | Molar Analysis - H2S | 403819 | Scaled Integer Format (10000 = 100%)
19 | 16 | Molar Analysis - H2 | 403820 | Scaled Integer Format (10000 = 100%)
20 | 16 | Molar Analysis - CO | 403821 | Scaled Integer Format (10000 = 100%)
21 | 16 | Molar Analysis - O2 | 403822 | Scaled Integer Format (10000 = 100%)
22 | 16 | Molar Analysis - iC4 | 403823 | Scaled Integer Format (10000 = 100%)
23 | 16 | Molar Analysis - C4 | 403824 | Scaled Integer Format (10000 = 100%)
24 | 16 | Molar Analysis - iC5 | 403825 | Scaled Integer Format (10000 = 100%)
25 | 16 | Molar Analysis - C5 | 403826 | Scaled Integer Format (10000 = 100%)
26 | 16 | Molar Analysis - C6 | 403827 | Scaled Integer Format (10000 = 100%)
27 | 16 | Molar Analysis - C7 | 403828 | Scaled Integer Format (10000 = 100%)
28 | 16 | Molar Analysis - C8 | 403829 | Scaled Integer Format (10000 = 100%)
29 | 16 | Molar Analysis - C9 | 403830 | Scaled Integer Format (10000 = 100%)
30 | 16 | Molar Analysis - C10 | 403831 | Scaled Integer Format (10000 = 100%)
31 | 16 | Molar Analysis - He | 403832 | Scaled Integer Format (10000 = 100%)
32 | 16 | Molar Analysis - Ar | 403833 | Scaled Integer Format (10000 = 100%)
33 | 16 | Molar Analysis - C5 (neo-p) | 403834 | Scaled Integer Format (10000 = 100%)
34 | 16 | Molar Analysis - Ux | 403835 | Scaled Integer Format (10000 = 100%)
35 | 16 | Molar Analysis - Uy | 403836 | Scaled Integer Format (10000 = 100%)
36 | 16 | Meter Signals - Reserved | 403837
37 | 16 | Meter Signals - Reserved | 403838
38 | 16 | Meter Signals - Reserved | 403839
39 | 16 | Meter Signals - Reserved | 403840
40 | 16 | Meter Signals - Reset Acc 1 | 403841
41 | 16 | Meter Signals - Reset Acc 2 | 403842
42 | 16 | Meter Signals - Reset Acc 3 | 403843
43 | 16 | Meter Signals - Reset Acc 4 | 403844
44 | 16 | Write Daily Archive | 403845
45 | 16 | Write Hourly Archive | 403846
46 | 16 | Meter Signals - Reserved | 403847
47 | 16 | Meter Signals - Reserved | 403848
48 | 16 | Meter Signals - Reserved | 403849
49 | 16 | Meter Signals - Reserved | 403850
50 | 16 | Meter Signals - Reserved | 403851
51 | 16 | Meter Signals - Reserved | 403852
52 | 16 | Analysis is Present | 403853
53 | 16 | Meter Archive Record Fetch | 403854 | (=0 signal not present)
54 | 16 | Meter Archive Record Age | 403855 | (=0 current)
55 | 16 | Meter Archive File Select | 403856 | (=0 daily, 1=hourly)

## Meter Results - Orifice & Gas
Meter 1 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Scan Count: process input | 400901
1 | 1 | Scan Count: calculation | 400902
2 | 1 | Meter in Alarm | 400903 | 0=no alarm
3 | 1 | Reserved | 400904
4 | 1 | Net Accumulator | 400905 | Long Integer Format
5 | 1 | Net Accumulator | 400906 | Long Integer Format
6 | 1 | Net Flow Rate | 400907 | Floating Point Format
7 | 1 | Net Flow Rate | 400908 | Floating Point Format
8 | 1 | Gross Flow Rate | 400909 | Floating Point Format
9 | 1 | Gross Flow Rate | 400910 | Floating Point Format
10 | 1 | Fpv | 400911 | Floating Point Format
11 | 1 | Fpv | 400912 | Floating Point Format
12 | 1 | Cprime | 400913 | Floating Point Format
13 | 1 | Cprime | 400914 | Floating Point Format
14 | 1 | Reserved | 400915
15 | 1 | Reserved | 400916
16 | 1 | Reserved | 400917
17 | 1 | Reserved | 400918
18 | 1 | Reserved | 400919
19 | 1 | Reserved | 400920
20 | 1 | Reserved | 400921
21 | 1 | Reserved | 400922
22 | 1 | Reserved | 400923
23 | 1 | Reserved | 400924
24 | 1 | Reserved | 400925
25 | 1 | Reserved | 400926
26 | 1 | Reserved | 400927
27 | 1 | Reserved | 400928
28 | 1 | Reserved | 400929
29 | 1 | Reserved | 400930
30 | 1 | Reserved | 400931
31 | 1 | Reserved | 400932
32 | 1 | Reserved | 400933
33 | 1 | Reserved | 400934
34 | 1 | Reserved | 400935
35 | 1 | Reserved | 400936
36 | 1 | Reserved | 400937
37 | 1 | Reserved | 400938
Meter 2 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Scan Count: process input | 401101
1 | 2 | Scan Count: calculation | 401102
2 | 2 | Meter in Alarm | 401103 | 0=no alarm
3 | 2 | Reserved | 401104
4 | 2 | Net Accumulator | 401105 | Long Integer Format
5 | 2 | Net Accumulator | 401106 | Long Integer Format
6 | 2 | Net Flow Rate | 401107 | Floating Point Format
7 | 2 | Net Flow Rate | 401108 | Floating Point Format
8 | 2 | Gross Flow Rate | 401109 | Floating Point Format
9 | 2 | Gross Flow Rate | 401110 | Floating Point Format
10 | 2 | Fpv | 401111 | Floating Point Format
11 | 2 | Fpv | 401112 | Floating Point Format
12 | 2 | Cprime | 401113 | Floating Point Format
13 | 2 | Cprime | 401114 | Floating Point Format
14 | 2 | Reserved | 401115
15 | 2 | Reserved | 401116
16 | 2 | Reserved | 401117
17 | 2 | Reserved | 401118
18 | 2 | Reserved | 401119
19 | 2 | Reserved | 401120
20 | 2 | Reserved | 401121
21 | 2 | Reserved | 401122
22 | 2 | Reserved | 401123
23 | 2 | Reserved | 401124
24 | 2 | Reserved | 401125
25 | 2 | Reserved | 401126
26 | 2 | Reserved | 401127
27 | 2 | Reserved | 401128
28 | 2 | Reserved | 401129
29 | 2 | Reserved | 401130
30 | 2 | Reserved | 401131
31 | 2 | Reserved | 401132
32 | 2 | Reserved | 401133
33 | 2 | Reserved | 401134
34 | 2 | Reserved | 401135
35 | 2 | Reserved | 401136
36 | 2 | Reserved | 401137
37 | 2 | Reserved | 401138
Meter 3 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Scan Count: process input | 401301
1 | 3 | Scan Count: calculation | 401302
2 | 3 | Meter in Alarm | 401303 | 0=no alarm
3 | 3 | Reserved | 401304
4 | 3 | Net Accumulator | 401305 | Long Integer Format
5 | 3 | Net Accumulator | 401306 | Long Integer Format
6 | 3 | Net Flow Rate | 401307 | Floating Point Format
7 | 3 | Net Flow Rate | 401308 | Floating Point Format
8 | 3 | Gross Flow Rate | 401309 | Floating Point Format
9 | 3 | Gross Flow Rate | 401310 | Floating Point Format
10 | 3 | Fpv | 401311 | Floating Point Format
11 | 3 | Fpv | 401312 | Floating Point Format
12 | 3 | Cprime | 401313 | Floating Point Format
13 | 3 | Cprime | 401314 | Floating Point Format
14 | 3 | Reserved | 401315
15 | 3 | Reserved | 401316
16 | 3 | Reserved | 401317
17 | 3 | Reserved | 401318
18 | 3 | Reserved | 401319
19 | 3 | Reserved | 401320
20 | 3 | Reserved | 401321
21 | 3 | Reserved | 401322
22 | 3 | Reserved | 401323
23 | 3 | Reserved | 401324
24 | 3 | Reserved | 401325
25 | 3 | Reserved | 401326
26 | 3 | Reserved | 401327
27 | 3 | Reserved | 401328
28 | 3 | Reserved | 401329
29 | 3 | Reserved | 401330
30 | 3 | Reserved | 401331
31 | 3 | Reserved | 401332
32 | 3 | Reserved | 401333
33 | 3 | Reserved | 401334
34 | 3 | Reserved | 401335
35 | 3 | Reserved | 401336
36 | 3 | Reserved | 401337
37 | 3 | Reserved | 401338
Meter 4 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Scan Count: process input | 401501
1 | 4 | Scan Count: calculation | 401502
2 | 4 | Meter in Alarm | 401503 | 0=no alarm
3 | 4 | Reserved | 401504
4 | 4 | Net Accumulator | 401505 | Long Integer Format
5 | 4 | Net Accumulator | 401506 | Long Integer Format
6 | 4 | Net Flow Rate | 401507 | Floating Point Format
7 | 4 | Net Flow Rate | 401508 | Floating Point Format
8 | 4 | Gross Flow Rate | 401509 | Floating Point Format
9 | 4 | Gross Flow Rate | 401510 | Floating Point Format
10 | 4 | Fpv | 401511 | Floating Point Format
11 | 4 | Fpv | 401512 | Floating Point Format
12 | 4 | Cprime | 401513 | Floating Point Format
13 | 4 | Cprime | 401514 | Floating Point Format
14 | 4 | Reserved | 401515
15 | 4 | Reserved | 401516
16 | 4 | Reserved | 401517
17 | 4 | Reserved | 401518
18 | 4 | Reserved | 401519
19 | 4 | Reserved | 401520
20 | 4 | Reserved | 401521
21 | 4 | Reserved | 401522
22 | 4 | Reserved | 401523
23 | 4 | Reserved | 401524
24 | 4 | Reserved | 401525
25 | 4 | Reserved | 401526
26 | 4 | Reserved | 401527
27 | 4 | Reserved | 401528
28 | 4 | Reserved | 401529
29 | 4 | Reserved | 401530
30 | 4 | Reserved | 401531
31 | 4 | Reserved | 401532
32 | 4 | Reserved | 401533
33 | 4 | Reserved | 401534
34 | 4 | Reserved | 401535
35 | 4 | Reserved | 401536
36 | 4 | Reserved | 401537
37 | 4 | Reserved | 401538
Meter 5 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Scan Count: process input | 401701
1 | 5 | Scan Count: calculation | 401702
2 | 5 | Meter in Alarm | 401703 | 0=no alarm
3 | 5 | Reserved | 401704
4 | 5 | Net Accumulator | 401705 | Long Integer Format
5 | 5 | Net Accumulator | 401706 | Long Integer Format
6 | 5 | Net Flow Rate | 401707 | Floating Point Format
7 | 5 | Net Flow Rate | 401708 | Floating Point Format
8 | 5 | Gross Flow Rate | 401709 | Floating Point Format
9 | 5 | Gross Flow Rate | 401710 | Floating Point Format
10 | 5 | Fpv | 401711 | Floating Point Format
11 | 5 | Fpv | 401712 | Floating Point Format
12 | 5 | Cprime | 401713 | Floating Point Format
13 | 5 | Cprime | 401714 | Floating Point Format
14 | 5 | Reserved | 401715
15 | 5 | Reserved | 401716
16 | 5 | Reserved | 401717
17 | 5 | Reserved | 401718
18 | 5 | Reserved | 401719
19 | 5 | Reserved | 401720
20 | 5 | Reserved | 401721
21 | 5 | Reserved | 401722
22 | 5 | Reserved | 401723
23 | 5 | Reserved | 401724
24 | 5 | Reserved | 401725
25 | 5 | Reserved | 401726
26 | 5 | Reserved | 401727
27 | 5 | Reserved | 401728
28 | 5 | Reserved | 401729
29 | 5 | Reserved | 401730
30 | 5 | Reserved | 401731
31 | 5 | Reserved | 401732
32 | 5 | Reserved | 401733
33 | 5 | Reserved | 401734
34 | 5 | Reserved | 401735
35 | 5 | Reserved | 401736
36 | 5 | Reserved | 401737
37 | 5 | Reserved | 401738
Meter 6 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Scan Count: process input | 401901
1 | 6 | Scan Count: calculation | 401902
2 | 6 | Meter in Alarm | 401903 | 0=no alarm
3 | 6 | Reserved | 401904
4 | 6 | Net Accumulator | 401905 | Long Integer Format
5 | 6 | Net Accumulator | 401906 | Long Integer Format
6 | 6 | Net Flow Rate | 401907 | Floating Point Format
7 | 6 | Net Flow Rate | 401908 | Floating Point Format
8 | 6 | Gross Flow Rate | 401909 | Floating Point Format
9 | 6 | Gross Flow Rate | 401910 | Floating Point Format
10 | 6 | Fpv | 401911 | Floating Point Format
11 | 6 | Fpv | 401912 | Floating Point Format
12 | 6 | Cprime | 401913 | Floating Point Format
13 | 6 | Cprime | 401914 | Floating Point Format
14 | 6 | Reserved | 401915
15 | 6 | Reserved | 401916
16 | 6 | Reserved | 401917
17 | 6 | Reserved | 401918
18 | 6 | Reserved | 401919
19 | 6 | Reserved | 401920
20 | 6 | Reserved | 401921
21 | 6 | Reserved | 401922
22 | 6 | Reserved | 401923
23 | 6 | Reserved | 401924
24 | 6 | Reserved | 401925
25 | 6 | Reserved | 401926
26 | 6 | Reserved | 401927
27 | 6 | Reserved | 401928
28 | 6 | Reserved | 401929
29 | 6 | Reserved | 401930
30 | 6 | Reserved | 401931
31 | 6 | Reserved | 401932
32 | 6 | Reserved | 401933
33 | 6 | Reserved | 401934
34 | 6 | Reserved | 401935
35 | 6 | Reserved | 401936
36 | 6 | Reserved | 401937
37 | 6 | Reserved | 401938
Meter 7 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Scan Count: process input | 402101
1 | 7 | Scan Count: calculation | 402102
2 | 7 | Meter in Alarm | 402103 | 0=no alarm
3 | 7 | Reserved | 402104
4 | 7 | Net Accumulator | 402105 | Long Integer Format
5 | 7 | Net Accumulator | 402106 | Long Integer Format
6 | 7 | Net Flow Rate | 402107 | Floating Point Format
7 | 7 | Net Flow Rate | 402108 | Floating Point Format
8 | 7 | Gross Flow Rate | 402109 | Floating Point Format
9 | 7 | Gross Flow Rate | 402110 | Floating Point Format
10 | 7 | Fpv | 402111 | Floating Point Format
11 | 7 | Fpv | 402112 | Floating Point Format
12 | 7 | Cprime | 402113 | Floating Point Format
13 | 7 | Cprime | 402114 | Floating Point Format
14 | 7 | Reserved | 402115
15 | 7 | Reserved | 402116
16 | 7 | Reserved | 402117
17 | 7 | Reserved | 402118
18 | 7 | Reserved | 402119
19 | 7 | Reserved | 402120
20 | 7 | Reserved | 402121
21 | 7 | Reserved | 402122
22 | 7 | Reserved | 402123
23 | 7 | Reserved | 402124
24 | 7 | Reserved | 402125
25 | 7 | Reserved | 402126
26 | 7 | Reserved | 402127
27 | 7 | Reserved | 402128
28 | 7 | Reserved | 402129
29 | 7 | Reserved | 402130
30 | 7 | Reserved | 402131
31 | 7 | Reserved | 402132
32 | 7 | Reserved | 402133
33 | 7 | Reserved | 402134
34 | 7 | Reserved | 402135
35 | 7 | Reserved | 402136
36 | 7 | Reserved | 402137
37 | 7 | Reserved | 402138
Meter 8 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Scan Count: process input | 402301
1 | 8 | Scan Count: calculation | 402302
2 | 8 | Meter in Alarm | 402303 | 0=no alarm
3 | 8 | Reserved | 402304
4 | 8 | Net Accumulator | 402305 | Long Integer Format
5 | 8 | Net Accumulator | 402306 | Long Integer Format
6 | 8 | Net Flow Rate | 402307 | Floating Point Format
7 | 8 | Net Flow Rate | 402308 | Floating Point Format
8 | 8 | Gross Flow Rate | 402309 | Floating Point Format
9 | 8 | Gross Flow Rate | 402310 | Floating Point Format
10 | 8 | Fpv | 402311 | Floating Point Format
11 | 8 | Fpv | 402312 | Floating Point Format
12 | 8 | Cprime | 402313 | Floating Point Format
13 | 8 | Cprime | 402314 | Floating Point Format
14 | 8 | Reserved | 402315
15 | 8 | Reserved | 402316
16 | 8 | Reserved | 402317
17 | 8 | Reserved | 402318
18 | 8 | Reserved | 402319
19 | 8 | Reserved | 402320
20 | 8 | Reserved | 402321
21 | 8 | Reserved | 402322
22 | 8 | Reserved | 402323
23 | 8 | Reserved | 402324
24 | 8 | Reserved | 402325
25 | 8 | Reserved | 402326
26 | 8 | Reserved | 402327
27 | 8 | Reserved | 402328
28 | 8 | Reserved | 402329
29 | 8 | Reserved | 402330
30 | 8 | Reserved | 402331
31 | 8 | Reserved | 402332
32 | 8 | Reserved | 402333
33 | 8 | Reserved | 402334
34 | 8 | Reserved | 402335
35 | 8 | Reserved | 402336
36 | 8 | Reserved | 402337
37 | 8 | Reserved | 402338
Meter 9 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Scan Count: process input | 402501
1 | 9 | Scan Count: calculation | 402502
2 | 9 | Meter in Alarm | 402503 | 0=no alarm
3 | 9 | Reserved | 402504
4 | 9 | Net Accumulator | 402505 | Long Integer Format
5 | 9 | Net Accumulator | 402506 | Long Integer Format
6 | 9 | Net Flow Rate | 402507 | Floating Point Format
7 | 9 | Net Flow Rate | 402508 | Floating Point Format
8 | 9 | Gross Flow Rate | 402509 | Floating Point Format
9 | 9 | Gross Flow Rate | 402510 | Floating Point Format
10 | 9 | Fpv | 402511 | Floating Point Format
11 | 9 | Fpv | 402512 | Floating Point Format
12 | 9 | Cprime | 402513 | Floating Point Format
13 | 9 | Cprime | 402514 | Floating Point Format
14 | 9 | Reserved | 402515
15 | 9 | Reserved | 402516
16 | 9 | Reserved | 402517
17 | 9 | Reserved | 402518
18 | 9 | Reserved | 402519
19 | 9 | Reserved | 402520
20 | 9 | Reserved | 402521
21 | 9 | Reserved | 402522
22 | 9 | Reserved | 402523
23 | 9 | Reserved | 402524
24 | 9 | Reserved | 402525
25 | 9 | Reserved | 402526
26 | 9 | Reserved | 402527
27 | 9 | Reserved | 402528
28 | 9 | Reserved | 402529
29 | 9 | Reserved | 402530
30 | 9 | Reserved | 402531
31 | 9 | Reserved | 402532
32 | 9 | Reserved | 402533
33 | 9 | Reserved | 402534
34 | 9 | Reserved | 402535
35 | 9 | Reserved | 402536
36 | 9 | Reserved | 402537
37 | 9 | Reserved | 402538
Meter 10 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Scan Count: process input | 402701
1 | 10 | Scan Count: calculation | 402702
2 | 10 | Meter in Alarm | 402703 | 0=no alarm
3 | 10 | Reserved | 402704
4 | 10 | Net Accumulator | 402705 | Long Integer Format
5 | 10 | Net Accumulator | 402706 | Long Integer Format
6 | 10 | Net Flow Rate | 402707 | Floating Point Format
7 | 10 | Net Flow Rate | 402708 | Floating Point Format
8 | 10 | Gross Flow Rate | 402709 | Floating Point Format
9 | 10 | Gross Flow Rate | 402710 | Floating Point Format
10 | 10 | Fpv | 402711 | Floating Point Format
11 | 10 | Fpv | 402712 | Floating Point Format
12 | 10 | Cprime | 402713 | Floating Point Format
13 | 10 | Cprime | 402714 | Floating Point Format
14 | 10 | Reserved | 402715
15 | 10 | Reserved | 402716
16 | 10 | Reserved | 402717
17 | 10 | Reserved | 402718
18 | 10 | Reserved | 402719
19 | 10 | Reserved | 402720
20 | 10 | Reserved | 402721
21 | 10 | Reserved | 402722
22 | 10 | Reserved | 402723
23 | 10 | Reserved | 402724
24 | 10 | Reserved | 402725
25 | 10 | Reserved | 402726
26 | 10 | Reserved | 402727
27 | 10 | Reserved | 402728
28 | 10 | Reserved | 402729
29 | 10 | Reserved | 402730
30 | 10 | Reserved | 402731
31 | 10 | Reserved | 402732
32 | 10 | Reserved | 402733
33 | 10 | Reserved | 402734
34 | 10 | Reserved | 402735
35 | 10 | Reserved | 402736
36 | 10 | Reserved | 402737
37 | 10 | Reserved | 402738
Meter 11 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Scan Count: process input | 402901
1 | 11 | Scan Count: calculation | 402902
2 | 11 | Meter in Alarm | 402903 | 0=no alarm
3 | 11 | Reserved | 402904
4 | 11 | Net Accumulator | 402905 | Long Integer Format
5 | 11 | Net Accumulator | 402906 | Long Integer Format
6 | 11 | Net Flow Rate | 402907 | Floating Point Format
7 | 11 | Net Flow Rate | 402908 | Floating Point Format
8 | 11 | Gross Flow Rate | 402909 | Floating Point Format
9 | 11 | Gross Flow Rate | 402910 | Floating Point Format
10 | 11 | Fpv | 402911 | Floating Point Format
11 | 11 | Fpv | 402912 | Floating Point Format
12 | 11 | Cprime | 402913 | Floating Point Format
13 | 11 | Cprime | 402914 | Floating Point Format
14 | 11 | Reserved | 402915
15 | 11 | Reserved | 402916
16 | 11 | Reserved | 402917
17 | 11 | Reserved | 402918
18 | 11 | Reserved | 402919
19 | 11 | Reserved | 402920
20 | 11 | Reserved | 402921
21 | 11 | Reserved | 402922
22 | 11 | Reserved | 402923
23 | 11 | Reserved | 402924
24 | 11 | Reserved | 402925
25 | 11 | Reserved | 402926
26 | 11 | Reserved | 402927
27 | 11 | Reserved | 402928
28 | 11 | Reserved | 402929
29 | 11 | Reserved | 402930
30 | 11 | Reserved | 402931
31 | 11 | Reserved | 402932
32 | 11 | Reserved | 402933
33 | 11 | Reserved | 402934
34 | 11 | Reserved | 402935
35 | 11 | Reserved | 402936
36 | 11 | Reserved | 402937
37 | 11 | Reserved | 402938
Meter 12 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Scan Count: process input | 403101
1 | 12 | Scan Count: calculation | 403102
2 | 12 | Meter in Alarm | 403103 | 0=no alarm
3 | 12 | Reserved | 403104
4 | 12 | Net Accumulator | 403105 | Long Integer Format
5 | 12 | Net Accumulator | 403106 | Long Integer Format
6 | 12 | Net Flow Rate | 403107 | Floating Point Format
7 | 12 | Net Flow Rate | 403108 | Floating Point Format
8 | 12 | Gross Flow Rate | 403109 | Floating Point Format
9 | 12 | Gross Flow Rate | 403110 | Floating Point Format
10 | 12 | Fpv | 403111 | Floating Point Format
11 | 12 | Fpv | 403112 | Floating Point Format
12 | 12 | Cprime | 403113 | Floating Point Format
13 | 12 | Cprime | 403114 | Floating Point Format
14 | 12 | Reserved | 403115
15 | 12 | Reserved | 403116
16 | 12 | Reserved | 403117
17 | 12 | Reserved | 403118
18 | 12 | Reserved | 403119
19 | 12 | Reserved | 403120
20 | 12 | Reserved | 403121
21 | 12 | Reserved | 403122
22 | 12 | Reserved | 403123
23 | 12 | Reserved | 403124
24 | 12 | Reserved | 403125
25 | 12 | Reserved | 403126
26 | 12 | Reserved | 403127
27 | 12 | Reserved | 403128
28 | 12 | Reserved | 403129
29 | 12 | Reserved | 403130
30 | 12 | Reserved | 403131
31 | 12 | Reserved | 403132
32 | 12 | Reserved | 403133
33 | 12 | Reserved | 403134
34 | 12 | Reserved | 403135
35 | 12 | Reserved | 403136
36 | 12 | Reserved | 403137
37 | 12 | Reserved | 403138
Meter 13 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Scan Count: process input | 403301
1 | 13 | Scan Count: calculation | 403302
2 | 13 | Meter in Alarm | 403303 | 0=no alarm
3 | 13 | Reserved | 403304
4 | 13 | Net Accumulator | 403305 | Long Integer Format
5 | 13 | Net Accumulator | 403306 | Long Integer Format
6 | 13 | Net Flow Rate | 403307 | Floating Point Format
7 | 13 | Net Flow Rate | 403308 | Floating Point Format
8 | 13 | Gross Flow Rate | 403309 | Floating Point Format
9 | 13 | Gross Flow Rate | 403310 | Floating Point Format
10 | 13 | Fpv | 403311 | Floating Point Format
11 | 13 | Fpv | 403312 | Floating Point Format
12 | 13 | Cprime | 403313 | Floating Point Format
13 | 13 | Cprime | 403314 | Floating Point Format
14 | 13 | Reserved | 403315
15 | 13 | Reserved | 403316
16 | 13 | Reserved | 403317
17 | 13 | Reserved | 403318
18 | 13 | Reserved | 403319
19 | 13 | Reserved | 403320
20 | 13 | Reserved | 403321
21 | 13 | Reserved | 403322
22 | 13 | Reserved | 403323
23 | 13 | Reserved | 403324
24 | 13 | Reserved | 403325
25 | 13 | Reserved | 403326
26 | 13 | Reserved | 403327
27 | 13 | Reserved | 403328
28 | 13 | Reserved | 403329
29 | 13 | Reserved | 403330
30 | 13 | Reserved | 403331
31 | 13 | Reserved | 403332
32 | 13 | Reserved | 403333
33 | 13 | Reserved | 403334
34 | 13 | Reserved | 403335
35 | 13 | Reserved | 403336
36 | 13 | Reserved | 403337
37 | 13 | Reserved | 403338
Meter 14 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Scan Count: process input | 403501
1 | 14 | Scan Count: calculation | 403502
2 | 14 | Meter in Alarm | 403503 | 0=no alarm
3 | 14 | Reserved | 403504
4 | 14 | Net Accumulator | 403505 | Long Integer Format
5 | 14 | Net Accumulator | 403506 | Long Integer Format
6 | 14 | Net Flow Rate | 403507 | Floating Point Format
7 | 14 | Net Flow Rate | 403508 | Floating Point Format
8 | 14 | Gross Flow Rate | 403509 | Floating Point Format
9 | 14 | Gross Flow Rate | 403510 | Floating Point Format
10 | 14 | Fpv | 403511 | Floating Point Format
11 | 14 | Fpv | 403512 | Floating Point Format
12 | 14 | Cprime | 403513 | Floating Point Format
13 | 14 | Cprime | 403514 | Floating Point Format
14 | 14 | Reserved | 403515
15 | 14 | Reserved | 403516
16 | 14 | Reserved | 403517
17 | 14 | Reserved | 403518
18 | 14 | Reserved | 403519
19 | 14 | Reserved | 403520
20 | 14 | Reserved | 403521
21 | 14 | Reserved | 403522
22 | 14 | Reserved | 403523
23 | 14 | Reserved | 403524
24 | 14 | Reserved | 403525
25 | 14 | Reserved | 403526
26 | 14 | Reserved | 403527
27 | 14 | Reserved | 403528
28 | 14 | Reserved | 403529
29 | 14 | Reserved | 403530
30 | 14 | Reserved | 403531
31 | 14 | Reserved | 403532
32 | 14 | Reserved | 403533
33 | 14 | Reserved | 403534
34 | 14 | Reserved | 403535
35 | 14 | Reserved | 403536
36 | 14 | Reserved | 403537
37 | 14 | Reserved | 403538
Meter 15 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Scan Count: process input | 403701
1 | 15 | Scan Count: calculation | 403702
2 | 15 | Meter in Alarm | 403703 | 0=no alarm
3 | 15 | Reserved | 403704
4 | 15 | Net Accumulator | 403705 | Long Integer Format
5 | 15 | Net Accumulator | 403706 | Long Integer Format
6 | 15 | Net Flow Rate | 403707 | Floating Point Format
7 | 15 | Net Flow Rate | 403708 | Floating Point Format
8 | 15 | Gross Flow Rate | 403709 | Floating Point Format
9 | 15 | Gross Flow Rate | 403710 | Floating Point Format
10 | 15 | Fpv | 403711 | Floating Point Format
11 | 15 | Fpv | 403712 | Floating Point Format
12 | 15 | Cprime | 403713 | Floating Point Format
13 | 15 | Cprime | 403714 | Floating Point Format
14 | 15 | Reserved | 403715
15 | 15 | Reserved | 403716
16 | 15 | Reserved | 403717
17 | 15 | Reserved | 403718
18 | 15 | Reserved | 403719
19 | 15 | Reserved | 403720
20 | 15 | Reserved | 403721
21 | 15 | Reserved | 403722
22 | 15 | Reserved | 403723
23 | 15 | Reserved | 403724
24 | 15 | Reserved | 403725
25 | 15 | Reserved | 403726
26 | 15 | Reserved | 403727
27 | 15 | Reserved | 403728
28 | 15 | Reserved | 403729
29 | 15 | Reserved | 403730
30 | 15 | Reserved | 403731
31 | 15 | Reserved | 403732
32 | 15 | Reserved | 403733
33 | 15 | Reserved | 403734
34 | 15 | Reserved | 403735
35 | 15 | Reserved | 403736
36 | 15 | Reserved | 403737
37 | 15 | Reserved | 403738
Meter 16 Results Orifice & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Scan Count: process input | 403901
1 | 16 | Scan Count: calculation | 403902
2 | 16 | Meter in Alarm | 403903 | 0=no alarm
3 | 16 | Reserved | 403904
4 | 16 | Net Accumulator | 403905 | Long Integer Format
5 | 16 | Net Accumulator | 403906 | Long Integer Format
6 | 16 | Net Flow Rate | 403907 | Floating Point Format
7 | 16 | Net Flow Rate | 403908 | Floating Point Format
8 | 16 | Gross Flow Rate | 403909 | Floating Point Format
9 | 16 | Gross Flow Rate | 403910 | Floating Point Format
10 | 16 | Fpv | 403911 | Floating Point Format
11 | 16 | Fpv | 403912 | Floating Point Format
12 | 16 | Cprime | 403913 | Floating Point Format
13 | 16 | Cprime | 403914 | Floating Point Format
14 | 16 | Reserved | 403915
15 | 16 | Reserved | 403916
16 | 16 | Reserved | 403917
17 | 16 | Reserved | 403918
18 | 16 | Reserved | 403919
19 | 16 | Reserved | 403920
20 | 16 | Reserved | 403921
21 | 16 | Reserved | 403922
22 | 16 | Reserved | 403923
23 | 16 | Reserved | 403924
24 | 16 | Reserved | 403925
25 | 16 | Reserved | 403926
26 | 16 | Reserved | 403927
27 | 16 | Reserved | 403928
28 | 16 | Reserved | 403929
29 | 16 | Reserved | 403930
30 | 16 | Reserved | 403931
31 | 16 | Reserved | 403932
32 | 16 | Reserved | 403933
33 | 16 | Reserved | 403934
34 | 16 | Reserved | 403935
35 | 16 | Reserved | 403936
36 | 16 | Reserved | 403937
37 | 16 | Reserved | 403938

## Meter Variables - Pulse & Gas
Meter 1 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Meter Disable | 400801
1 | 1 | Reserved | 400802
2 | 1 | Temperature | 400803 | Floating Point Format
3 | 1 | Temperature | 400804 | Floating Point Format
4 | 1 | Pressure | 400805 | Floating Point Format
5 | 1 | Pressure | 400806 | Floating Point Format
6 | 1 | Meter Pulses | 400807 | Double Integer Format
7 | 1 | Meter Pulses | 400808 | Double Integer Format
8 | 1 | Reserved | 400809
9 | 1 | Reserved | 400810
10 | 1 | Pulse Frequency | 400811 | Floating Point Format
11 | 1 | Pulse Frequency | 400812 | Floating Point Format
12 | 1 | Molar Analysis - C1 | 400813 | Scaled Integer Format (10000 = 100%)
13 | 1 | Molar Analysis - N2 | 400814 | Scaled Integer Format (10000 = 100%)
14 | 1 | Molar Analysis - CO2 | 400815 | Scaled Integer Format (10000 = 100%)
15 | 1 | Molar Analysis - C2 | 400816 | Scaled Integer Format (10000 = 100%)
16 | 1 | Molar Analysis - C3 | 400817 | Scaled Integer Format (10000 = 100%)
17 | 1 | Molar Analysis - H2O | 400818 | Scaled Integer Format (10000 = 100%)
18 | 1 | Molar Analysis - H2S | 400819 | Scaled Integer Format (10000 = 100%)
19 | 1 | Molar Analysis - H2 | 400820 | Scaled Integer Format (10000 = 100%)
20 | 1 | Molar Analysis - CO | 400821 | Scaled Integer Format (10000 = 100%)
21 | 1 | Molar Analysis - O2 | 400822 | Scaled Integer Format (10000 = 100%)
22 | 1 | Molar Analysis - iC4 | 400823 | Scaled Integer Format (10000 = 100%)
23 | 1 | Molar Analysis - C4 | 400824 | Scaled Integer Format (10000 = 100%)
24 | 1 | Molar Analysis - iC5 | 400825 | Scaled Integer Format (10000 = 100%)
25 | 1 | Molar Analysis - C5 | 400826 | Scaled Integer Format (10000 = 100%)
26 | 1 | Molar Analysis - C6 | 400827 | Scaled Integer Format (10000 = 100%)
27 | 1 | Molar Analysis - C7 | 400828 | Scaled Integer Format (10000 = 100%)
28 | 1 | Molar Analysis - C8 | 400829 | Scaled Integer Format (10000 = 100%)
29 | 1 | Molar Analysis - C9 | 400830 | Scaled Integer Format (10000 = 100%)
30 | 1 | Molar Analysis - C10 | 400831 | Scaled Integer Format (10000 = 100%)
31 | 1 | Molar Analysis - He | 400832 | Scaled Integer Format (10000 = 100%)
32 | 1 | Molar Analysis - Ar | 400833 | Scaled Integer Format (10000 = 100%)
33 | 1 | Molar Analysis - C5 (neo-p) | 400834 | Scaled Integer Format (10000 = 100%)
34 | 1 | Molar Analysis - Ux | 400835 | Scaled Integer Format (10000 = 100%)
35 | 1 | Molar Analysis - Uy | 400836 | Scaled Integer Format (10000 = 100%)
36 | 1 | Meter Signals - Reserved | 400837
37 | 1 | Meter Signals - Reserved | 400838
38 | 1 | Meter Signals - Reserved | 400839
39 | 1 | Meter Signals - Reserved | 400840
40 | 1 | Meter Signals - Reset Acc 1 | 400841
41 | 1 | Meter Signals - Reset Acc 2 | 400842
42 | 1 | Meter Signals - Reset Acc 3 | 400843
43 | 1 | Meter Signals - Reset Acc 4 | 400844
44 | 1 | Write Daily Archive | 400845
45 | 1 | Write Hourly Archive | 400846
46 | 1 | Meter Signals - Reserved | 400847
47 | 1 | Meter Signals - Reserved | 400848
48 | 1 | Meter Signals - Reserved | 400849
49 | 1 | Meter Signals - Reserved | 400850
50 | 1 | Meter Signals - Reserved | 400851
51 | 1 | Meter Signals - Reserved | 400852
52 | 1 | Analysis is Present | 400853
53 | 1 | Meter Archive Record Fetch | 400854 | (=0 signal not present)
54 | 1 | Meter Archive Record Age | 400855 | (=0 current)
55 | 1 | Meter Archive File Select | 400856 | (=0 daily, 1=hourly)
Meter 2 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Meter Disable | 401001
1 | 2 | Reserved | 401002
2 | 2 | Temperature | 401003 | Floating Point Format
3 | 2 | Temperature | 401004 | Floating Point Format
4 | 2 | Pressure | 401005 | Floating Point Format
5 | 2 | Pressure | 401006 | Floating Point Format
6 | 2 | Pulse Count | 401007 | Long Integer
7 | 2 | Pulse Count | 401008 | Long Integer
8 | 2 | Reserved | 401009
9 | 2 | Reserved | 401010
10 | 2 | Pulse Frequency | 401011 | Floating Point Format
11 | 2 | Pulse Frequency | 401012 | Floating Point Format
12 | 2 | Molar Analysis - C1 | 401013 | Scaled Integer Format (10000 = 100%)
13 | 2 | Molar Analysis - N2 | 401014 | Scaled Integer Format (10000 = 100%)
14 | 2 | Molar Analysis - CO2 | 401015 | Scaled Integer Format (10000 = 100%)
15 | 2 | Molar Analysis - C2 | 401016 | Scaled Integer Format (10000 = 100%)
16 | 2 | Molar Analysis - C3 | 401017 | Scaled Integer Format (10000 = 100%)
17 | 2 | Molar Analysis - H2O | 401018 | Scaled Integer Format (10000 = 100%)
18 | 2 | Molar Analysis - H2S | 401019 | Scaled Integer Format (10000 = 100%)
19 | 2 | Molar Analysis - H2 | 401020 | Scaled Integer Format (10000 = 100%)
20 | 2 | Molar Analysis - CO | 401021 | Scaled Integer Format (10000 = 100%)
21 | 2 | Molar Analysis - O2 | 401022 | Scaled Integer Format (10000 = 100%)
22 | 2 | Molar Analysis - iC4 | 401023 | Scaled Integer Format (10000 = 100%)
23 | 2 | Molar Analysis - C4 | 401024 | Scaled Integer Format (10000 = 100%)
24 | 2 | Molar Analysis - iC5 | 401025 | Scaled Integer Format (10000 = 100%)
25 | 2 | Molar Analysis - C5 | 401026 | Scaled Integer Format (10000 = 100%)
26 | 2 | Molar Analysis - C6 | 401027 | Scaled Integer Format (10000 = 100%)
27 | 2 | Molar Analysis - C7 | 401028 | Scaled Integer Format (10000 = 100%)
28 | 2 | Molar Analysis - C8 | 401029 | Scaled Integer Format (10000 = 100%)
29 | 2 | Molar Analysis - C9 | 401030 | Scaled Integer Format (10000 = 100%)
30 | 2 | Molar Analysis - C10 | 401031 | Scaled Integer Format (10000 = 100%)
31 | 2 | Molar Analysis - He | 401032 | Scaled Integer Format (10000 = 100%)
32 | 2 | Molar Analysis - Ar | 401033 | Scaled Integer Format (10000 = 100%)
33 | 2 | Molar Analysis - C5 (neo-p) | 401034 | Scaled Integer Format (10000 = 100%)
34 | 2 | Molar Analysis - Ux | 401035 | Scaled Integer Format (10000 = 100%)
35 | 2 | Molar Analysis - Uy | 401036 | Scaled Integer Format (10000 = 100%)
36 | 2 | Meter Signals - Reserved | 401037
37 | 2 | Meter Signals - Reserved | 401038
38 | 2 | Meter Signals - Reserved | 401039
39 | 2 | Meter Signals - Reserved | 401040
40 | 2 | Meter Signals - Reset Acc 1 | 401041
41 | 2 | Meter Signals - Reset Acc 2 | 401042
42 | 2 | Meter Signals - Reset Acc 3 | 401043
43 | 2 | Meter Signals - Reset Acc 4 | 401044
44 | 2 | Write Daily Archive | 401045
45 | 2 | Write Hourly Archive | 401046
46 | 2 | Meter Signals - Reserved | 401047
47 | 2 | Meter Signals - Reserved | 401048
48 | 2 | Meter Signals - Reserved | 401049
49 | 2 | Meter Signals - Reserved | 401050
50 | 2 | Meter Signals - Reserved | 401051
51 | 2 | Meter Signals - Reserved | 401052
52 | 2 | Analysis is Present | 401053
53 | 2 | Meter Archive Record Fetch | 401054 | (=0 signal not present)
54 | 2 | Meter Archive Record Age | 401055 | (=0 current)
55 | 2 | Meter Archive File Select | 401056 | (=0 daily, 1=hourly)
Meter 3 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Meter Disable | 401201
1 | 3 | Reserved | 401202
2 | 3 | Temperature | 401203 | Floating Point Format
3 | 3 | Temperature | 401204 | Floating Point Format
4 | 3 | Pressure | 401205 | Floating Point Format
5 | 3 | Pressure | 401206 | Floating Point Format
6 | 3 | Differential Pressure | 401207 | Long Integer Format
7 | 3 | Differential Pressure | 401208 | Long Integer Format
8 | 3 | Reserved | 401209
9 | 3 | Reserved | 401210
10 | 3 | Pulse Frequency | 401211 | Floating Point Format
11 | 3 | Pulse Frequency | 401212 | Floating Point Format
12 | 3 | Molar Analysis - C1 | 401213 | Scaled Integer Format (10000 = 100%)
13 | 3 | Molar Analysis - N2 | 401214 | Scaled Integer Format (10000 = 100%)
14 | 3 | Molar Analysis - CO2 | 401215 | Scaled Integer Format (10000 = 100%)
15 | 3 | Molar Analysis - C2 | 401216 | Scaled Integer Format (10000 = 100%)
16 | 3 | Molar Analysis - C3 | 401217 | Scaled Integer Format (10000 = 100%)
17 | 3 | Molar Analysis - H2O | 401218 | Scaled Integer Format (10000 = 100%)
18 | 3 | Molar Analysis - H2S | 401219 | Scaled Integer Format (10000 = 100%)
19 | 3 | Molar Analysis - H2 | 401220 | Scaled Integer Format (10000 = 100%)
20 | 3 | Molar Analysis - CO | 401221 | Scaled Integer Format (10000 = 100%)
21 | 3 | Molar Analysis - O2 | 401222 | Scaled Integer Format (10000 = 100%)
22 | 3 | Molar Analysis - iC4 | 401223 | Scaled Integer Format (10000 = 100%)
23 | 3 | Molar Analysis - C4 | 401224 | Scaled Integer Format (10000 = 100%)
24 | 3 | Molar Analysis - iC5 | 401225 | Scaled Integer Format (10000 = 100%)
25 | 3 | Molar Analysis - C5 | 401226 | Scaled Integer Format (10000 = 100%)
26 | 3 | Molar Analysis - C6 | 401227 | Scaled Integer Format (10000 = 100%)
27 | 3 | Molar Analysis - C7 | 401228 | Scaled Integer Format (10000 = 100%)
28 | 3 | Molar Analysis - C8 | 401229 | Scaled Integer Format (10000 = 100%)
29 | 3 | Molar Analysis - C9 | 401230 | Scaled Integer Format (10000 = 100%)
30 | 3 | Molar Analysis - C10 | 401231 | Scaled Integer Format (10000 = 100%)
31 | 3 | Molar Analysis - He | 401232 | Scaled Integer Format (10000 = 100%)
32 | 3 | Molar Analysis - Ar | 401233 | Scaled Integer Format (10000 = 100%)
33 | 3 | Molar Analysis - C5 (neo-p) | 401234 | Scaled Integer Format (10000 = 100%)
34 | 3 | Molar Analysis - Ux | 401235 | Scaled Integer Format (10000 = 100%)
35 | 3 | Molar Analysis - Uy | 401236 | Scaled Integer Format (10000 = 100%)
36 | 3 | Meter Signals - Reserved | 401237
37 | 3 | Meter Signals - Reserved | 401238
38 | 3 | Meter Signals - Reserved | 401239
39 | 3 | Meter Signals - Reserved | 401240
40 | 3 | Meter Signals - Reset Acc 1 | 401241
41 | 3 | Meter Signals - Reset Acc 2 | 401242
42 | 3 | Meter Signals - Reset Acc 3 | 401243
43 | 3 | Meter Signals - Reset Acc 4 | 401244
44 | 3 | Write Daily Archive | 401245
45 | 3 | Write Hourly Archive | 401246
46 | 3 | Meter Signals - Reserved | 401247
47 | 3 | Meter Signals - Reserved | 401248
48 | 3 | Meter Signals - Reserved | 401249
49 | 3 | Meter Signals - Reserved | 401250
50 | 3 | Meter Signals - Reserved | 401251
51 | 3 | Meter Signals - Reserved | 401252
52 | 3 | Analysis is Present | 401253
53 | 3 | Meter Archive Record Fetch | 401254 | (=0 signal not present)
54 | 3 | Meter Archive Record Age | 401255 | (=0 current)
55 | 3 | Meter Archive File Select | 401256 | (=0 daily, 1=hourly)
Meter 4 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Meter Disable | 401401
1 | 4 | Reserved | 401402
2 | 4 | Temperature | 401403 | Floating Point Format
3 | 4 | Temperature | 401404 | Floating Point Format
4 | 4 | Pressure | 401405 | Floating Point Format
5 | 4 | Pressure | 401406 | Floating Point Format
6 | 4 | Pulse Count | 401407 | Long Integer Format
7 | 4 | Pulse Count | 401408 | Long Integer Format
8 | 4 | Reserved | 401409
9 | 4 | Reserved | 401410
10 | 4 | Pulse Frequency | 401411 | Floating Point Format
11 | 4 | Pulse Frequency | 401412 | Floating Point Format
12 | 4 | Molar Analysis - C1 | 401413 | Scaled Integer Format (10000 = 100%)
13 | 4 | Molar Analysis - N2 | 401414 | Scaled Integer Format (10000 = 100%)
14 | 4 | Molar Analysis - CO2 | 401415 | Scaled Integer Format (10000 = 100%)
15 | 4 | Molar Analysis - C2 | 401416 | Scaled Integer Format (10000 = 100%)
16 | 4 | Molar Analysis - C3 | 401417 | Scaled Integer Format (10000 = 100%)
17 | 4 | Molar Analysis - H2O | 401418 | Scaled Integer Format (10000 = 100%)
18 | 4 | Molar Analysis - H2S | 401419 | Scaled Integer Format (10000 = 100%)
19 | 4 | Molar Analysis - H2 | 401420 | Scaled Integer Format (10000 = 100%)
20 | 4 | Molar Analysis - CO | 401421 | Scaled Integer Format (10000 = 100%)
21 | 4 | Molar Analysis - O2 | 401422 | Scaled Integer Format (10000 = 100%)
22 | 4 | Molar Analysis - iC4 | 401423 | Scaled Integer Format (10000 = 100%)
23 | 4 | Molar Analysis - C4 | 401424 | Scaled Integer Format (10000 = 100%)
24 | 4 | Molar Analysis - iC5 | 401425 | Scaled Integer Format (10000 = 100%)
25 | 4 | Molar Analysis - C5 | 401426 | Scaled Integer Format (10000 = 100%)
26 | 4 | Molar Analysis - C6 | 401427 | Scaled Integer Format (10000 = 100%)
27 | 4 | Molar Analysis - C7 | 401428 | Scaled Integer Format (10000 = 100%)
28 | 4 | Molar Analysis - C8 | 401429 | Scaled Integer Format (10000 = 100%)
29 | 4 | Molar Analysis - C9 | 401430 | Scaled Integer Format (10000 = 100%)
30 | 4 | Molar Analysis - C10 | 401431 | Scaled Integer Format (10000 = 100%)
31 | 4 | Molar Analysis - He | 401432 | Scaled Integer Format (10000 = 100%)
32 | 4 | Molar Analysis - Ar | 401433 | Scaled Integer Format (10000 = 100%)
33 | 4 | Molar Analysis - C5 (neo-p) | 401434 | Scaled Integer Format (10000 = 100%)
34 | 4 | Molar Analysis - Ux | 401435 | Scaled Integer Format (10000 = 100%)
35 | 4 | Molar Analysis - Uy | 401436 | Scaled Integer Format (10000 = 100%)
36 | 4 | Meter Signals - Reserved | 401437
37 | 4 | Meter Signals - Reserved | 401438
38 | 4 | Meter Signals - Reserved | 401439
39 | 4 | Meter Signals - Reserved | 401440
40 | 4 | Meter Signals - Reset Acc 1 | 401441
41 | 4 | Meter Signals - Reset Acc 2 | 401442
42 | 4 | Meter Signals - Reset Acc 3 | 401443
43 | 4 | Meter Signals - Reset Acc 4 | 401444
44 | 4 | Write Daily Archive | 401445
45 | 4 | Write Hourly Archive | 401446
46 | 4 | Meter Signals - Reserved | 401447
47 | 4 | Meter Signals - Reserved | 401448
48 | 4 | Meter Signals - Reserved | 401449
49 | 4 | Meter Signals - Reserved | 401450
50 | 4 | Meter Signals - Reserved | 401451
51 | 4 | Meter Signals - Reserved | 401452
52 | 4 | Analysis is Present | 401453
53 | 4 | Meter Archive Record Fetch | 401454 | (=0 signal not present)
54 | 4 | Meter Archive Record Age | 401455 | (=0 current)
55 | 4 | Meter Archive File Select | 401456 | (=0 daily, 1=hourly)
Meter 5 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Meter Disable | 401601
1 | 5 | Reserved | 401602
2 | 5 | Temperature | 401603 | Floating Point Format
3 | 5 | Temperature | 401604 | Floating Point Format
4 | 5 | Pressure | 401605 | Floating Point Format
5 | 5 | Pressure | 401606 | Floating Point Format
6 | 5 | Differential Pressure | 401607 | Long Integer Format
7 | 5 | Differential Pressure | 401608 | Long Integer Format
8 | 5 | Reserved | 401609
9 | 5 | Reserved | 401610
10 | 5 | Pulse Frequency | 401611 | Floating Point Format
11 | 5 | Pulse Frequency | 401612 | Floating Point Format
12 | 5 | Molar Analysis - C1 | 401613 | Scaled Integer Format (10000 = 100%)
13 | 5 | Molar Analysis - N2 | 401614 | Scaled Integer Format (10000 = 100%)
14 | 5 | Molar Analysis - CO2 | 401615 | Scaled Integer Format (10000 = 100%)
15 | 5 | Molar Analysis - C2 | 401616 | Scaled Integer Format (10000 = 100%)
16 | 5 | Molar Analysis - C3 | 401617 | Scaled Integer Format (10000 = 100%)
17 | 5 | Molar Analysis - H2O | 401618 | Scaled Integer Format (10000 = 100%)
18 | 5 | Molar Analysis - H2S | 401619 | Scaled Integer Format (10000 = 100%)
19 | 5 | Molar Analysis - H2 | 401620 | Scaled Integer Format (10000 = 100%)
20 | 5 | Molar Analysis - CO | 401621 | Scaled Integer Format (10000 = 100%)
21 | 5 | Molar Analysis - O2 | 401622 | Scaled Integer Format (10000 = 100%)
22 | 5 | Molar Analysis - iC4 | 401623 | Scaled Integer Format (10000 = 100%)
23 | 5 | Molar Analysis - C4 | 401624 | Scaled Integer Format (10000 = 100%)
24 | 5 | Molar Analysis - iC5 | 401625 | Scaled Integer Format (10000 = 100%)
25 | 5 | Molar Analysis - C5 | 401626 | Scaled Integer Format (10000 = 100%)
26 | 5 | Molar Analysis - C6 | 401627 | Scaled Integer Format (10000 = 100%)
27 | 5 | Molar Analysis - C7 | 401628 | Scaled Integer Format (10000 = 100%)
28 | 5 | Molar Analysis - C8 | 401629 | Scaled Integer Format (10000 = 100%)
29 | 5 | Molar Analysis - C9 | 401630 | Scaled Integer Format (10000 = 100%)
30 | 5 | Molar Analysis - C10 | 401631 | Scaled Integer Format (10000 = 100%)
31 | 5 | Molar Analysis - He | 401632 | Scaled Integer Format (10000 = 100%)
32 | 5 | Molar Analysis - Ar | 401633 | Scaled Integer Format (10000 = 100%)
33 | 5 | Molar Analysis - C5 (neo-p) | 401634 | Scaled Integer Format (10000 = 100%)
34 | 5 | Molar Analysis - Ux | 401635 | Scaled Integer Format (10000 = 100%)
35 | 5 | Molar Analysis - Uy | 401636 | Scaled Integer Format (10000 = 100%)
36 | 5 | Meter Signals - Reserved | 401637
37 | 5 | Meter Signals - Reserved | 401638
38 | 5 | Meter Signals - Reserved | 401639
39 | 5 | Meter Signals - Reserved | 401640
40 | 5 | Meter Signals - Reset Acc 1 | 401641
41 | 5 | Meter Signals - Reset Acc 2 | 401642
42 | 5 | Meter Signals - Reset Acc 3 | 401643
43 | 5 | Meter Signals - Reset Acc 4 | 401644
44 | 5 | Write Daily Archive | 401645
45 | 5 | Write Hourly Archive | 401646
46 | 5 | Meter Signals - Reserved | 401647
47 | 5 | Meter Signals - Reserved | 401648
48 | 5 | Meter Signals - Reserved | 401649
49 | 5 | Meter Signals - Reserved | 401650
50 | 5 | Meter Signals - Reserved | 401651
51 | 5 | Meter Signals - Reserved | 401652
52 | 5 | Analysis is Present | 401653
53 | 5 | Meter Archive Record Fetch | 401654 | (=0 signal not present)
54 | 5 | Meter Archive Record Age | 401655 | (=0 current)
55 | 5 | Meter Archive File Select | 401656 | (=0 daily, 1=hourly)
Meter 6 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Meter Disable | 401801
1 | 6 | Reserved | 401802
2 | 6 | Temperature | 401803 | Floating Point Format
3 | 6 | Temperature | 401804 | Floating Point Format
4 | 6 | Pressure | 401805 | Floating Point Format
5 | 6 | Pressure | 401806 | Floating Point Format
6 | 6 | Pulse Count | 401807 | Long Integer Format
7 | 6 | Pulse Count | 401808 | Long Integer Format
8 | 6 | Reserved | 401809
9 | 6 | Reserved | 401810
10 | 6 | Pulse Frequency | 401811 | Floating Point Format
11 | 6 | Pulse Frequency | 401812 | Floating Point Format
12 | 6 | Molar Analysis - C1 | 401813 | Scaled Integer Format (10000 = 100%)
13 | 6 | Molar Analysis - N2 | 401814 | Scaled Integer Format (10000 = 100%)
14 | 6 | Molar Analysis - CO2 | 401815 | Scaled Integer Format (10000 = 100%)
15 | 6 | Molar Analysis - C2 | 401816 | Scaled Integer Format (10000 = 100%)
16 | 6 | Molar Analysis - C3 | 401817 | Scaled Integer Format (10000 = 100%)
17 | 6 | Molar Analysis - H2O | 401818 | Scaled Integer Format (10000 = 100%)
18 | 6 | Molar Analysis - H2S | 401819 | Scaled Integer Format (10000 = 100%)
19 | 6 | Molar Analysis - H2 | 401820 | Scaled Integer Format (10000 = 100%)
20 | 6 | Molar Analysis - CO | 401821 | Scaled Integer Format (10000 = 100%)
21 | 6 | Molar Analysis - O2 | 401822 | Scaled Integer Format (10000 = 100%)
22 | 6 | Molar Analysis - iC4 | 401823 | Scaled Integer Format (10000 = 100%)
23 | 6 | Molar Analysis - C4 | 401824 | Scaled Integer Format (10000 = 100%)
24 | 6 | Molar Analysis - iC5 | 401825 | Scaled Integer Format (10000 = 100%)
25 | 6 | Molar Analysis - C5 | 401826 | Scaled Integer Format (10000 = 100%)
26 | 6 | Molar Analysis - C6 | 401827 | Scaled Integer Format (10000 = 100%)
27 | 6 | Molar Analysis - C7 | 401828 | Scaled Integer Format (10000 = 100%)
28 | 6 | Molar Analysis - C8 | 401829 | Scaled Integer Format (10000 = 100%)
29 | 6 | Molar Analysis - C9 | 401830 | Scaled Integer Format (10000 = 100%)
30 | 6 | Molar Analysis - C10 | 401831 | Scaled Integer Format (10000 = 100%)
31 | 6 | Molar Analysis - He | 401832 | Scaled Integer Format (10000 = 100%)
32 | 6 | Molar Analysis - Ar | 401833 | Scaled Integer Format (10000 = 100%)
33 | 6 | Molar Analysis - C5 (neo-p) | 401834 | Scaled Integer Format (10000 = 100%)
34 | 6 | Molar Analysis - Ux | 401835 | Scaled Integer Format (10000 = 100%)
35 | 6 | Molar Analysis - Uy | 401836 | Scaled Integer Format (10000 = 100%)
36 | 6 | Meter Signals - Reserved | 401837
37 | 6 | Meter Signals - Reserved | 401838
38 | 6 | Meter Signals - Reserved | 401839
39 | 6 | Meter Signals - Reserved | 401840
40 | 6 | Meter Signals - Reset Acc 1 | 401841
41 | 6 | Meter Signals - Reset Acc 2 | 401842
42 | 6 | Meter Signals - Reset Acc 3 | 401843
43 | 6 | Meter Signals - Reset Acc 4 | 401844
44 | 6 | Write Daily Archive | 401845
45 | 6 | Write Hourly Archive | 401846
46 | 6 | Meter Signals - Reserved | 401847
47 | 6 | Meter Signals - Reserved | 401848
48 | 6 | Meter Signals - Reserved | 401849
49 | 6 | Meter Signals - Reserved | 401850
50 | 6 | Meter Signals - Reserved | 401851
51 | 6 | Meter Signals - Reserved | 401852
52 | 6 | Analysis is Present | 401853
53 | 6 | Meter Archive Record Fetch | 401854 | (=0 signal not present)
54 | 6 | Meter Archive Record Age | 401855 | (=0 current)
55 | 6 | Meter Archive File Select | 401856 | (=0 daily, 1=hourly)
Meter 7 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Meter Disable | 402001
1 | 7 | Reserved | 402002
2 | 7 | Temperature | 402003 | Floating Point Format
3 | 7 | Temperature | 402004 | Floating Point Format
4 | 7 | Pressure | 402005 | Floating Point Format
5 | 7 | Pressure | 402006 | Floating Point Format
6 | 7 | Pulse Count | 402007 | Long Integer Format
7 | 7 | Pulse Count | 402008 | Long Integer Format
8 | 7 | Reserved | 402009
9 | 7 | Reserved | 402010
10 | 7 | Pulse Frequency | 402011 | Floating Point Format
11 | 7 | Pulse Frequency | 402012 | Floating Point Format
12 | 7 | Molar Analysis - C1 | 402013 | Scaled Integer Format (10000 = 100%)
13 | 7 | Molar Analysis - N2 | 402014 | Scaled Integer Format (10000 = 100%)
14 | 7 | Molar Analysis - CO2 | 402015 | Scaled Integer Format (10000 = 100%)
15 | 7 | Molar Analysis - C2 | 402016 | Scaled Integer Format (10000 = 100%)
16 | 7 | Molar Analysis - C3 | 402017 | Scaled Integer Format (10000 = 100%)
17 | 7 | Molar Analysis - H2O | 402018 | Scaled Integer Format (10000 = 100%)
18 | 7 | Molar Analysis - H2S | 402019 | Scaled Integer Format (10000 = 100%)
19 | 7 | Molar Analysis - H2 | 402020 | Scaled Integer Format (10000 = 100%)
20 | 7 | Molar Analysis - CO | 402021 | Scaled Integer Format (10000 = 100%)
21 | 7 | Molar Analysis - O2 | 402022 | Scaled Integer Format (10000 = 100%)
22 | 7 | Molar Analysis - iC4 | 402023 | Scaled Integer Format (10000 = 100%)
23 | 7 | Molar Analysis - C4 | 402024 | Scaled Integer Format (10000 = 100%)
24 | 7 | Molar Analysis - iC5 | 402025 | Scaled Integer Format (10000 = 100%)
25 | 7 | Molar Analysis - C5 | 402026 | Scaled Integer Format (10000 = 100%)
26 | 7 | Molar Analysis - C6 | 402027 | Scaled Integer Format (10000 = 100%)
27 | 7 | Molar Analysis - C7 | 402028 | Scaled Integer Format (10000 = 100%)
28 | 7 | Molar Analysis - C8 | 402029 | Scaled Integer Format (10000 = 100%)
29 | 7 | Molar Analysis - C9 | 402030 | Scaled Integer Format (10000 = 100%)
30 | 7 | Molar Analysis - C10 | 402031 | Scaled Integer Format (10000 = 100%)
31 | 7 | Molar Analysis - He | 402032 | Scaled Integer Format (10000 = 100%)
32 | 7 | Molar Analysis - Ar | 402033 | Scaled Integer Format (10000 = 100%)
33 | 7 | Molar Analysis - C5 (neo-p) | 402034 | Scaled Integer Format (10000 = 100%)
34 | 7 | Molar Analysis - Ux | 402035 | Scaled Integer Format (10000 = 100%)
35 | 7 | Molar Analysis - Uy | 402036 | Scaled Integer Format (10000 = 100%)
36 | 7 | Meter Signals - Reserved | 402037
37 | 7 | Meter Signals - Reserved | 402038
38 | 7 | Meter Signals - Reserved | 402039
39 | 7 | Meter Signals - Reserved | 402040
40 | 7 | Meter Signals - Reset Acc 1 | 402041
41 | 7 | Meter Signals - Reset Acc 2 | 402042
42 | 7 | Meter Signals - Reset Acc 3 | 402043
43 | 7 | Meter Signals - Reset Acc 4 | 402044
44 | 7 | Write Daily Archive | 402045
45 | 7 | Write Hourly Archive | 402046
46 | 7 | Meter Signals - Reserved | 402047
47 | 7 | Meter Signals - Reserved | 402048
48 | 7 | Meter Signals - Reserved | 402049
49 | 7 | Meter Signals - Reserved | 402050
50 | 7 | Meter Signals - Reserved | 402051
51 | 7 | Meter Signals - Reserved | 402052
52 | 7 | Analysis is Present | 402053
53 | 7 | Meter Archive Record Fetch | 402054 | (=0 signal not present)
54 | 7 | Meter Archive Record Age | 402055 | (=0 current)
55 | 7 | Meter Archive File Select | 402056 | (=0 daily, 1=hourly)
Meter 8 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Meter Disable | 402201
1 | 8 | Reserved | 402202
2 | 8 | Temperature | 402203 | Floating Point Format
3 | 8 | Temperature | 402204 | Floating Point Format
4 | 8 | Pressure | 402205 | Floating Point Format
5 | 8 | Pressure | 402206 | Floating Point Format
6 | 8 | Pulse Count | 402207 | Long Integer Format
7 | 8 | Pulse Count | 402208 | Long Integer Format
8 | 8 | Reserved | 402209
9 | 8 | Reserved | 402210
10 | 8 | Pulse Frequency | 402211 | Floating Point Format
11 | 8 | Pulse Frequency | 402212 | Floating Point Format
12 | 8 | Molar Analysis - C1 | 402213 | Scaled Integer Format (10000 = 100%)
13 | 8 | Molar Analysis - N2 | 402214 | Scaled Integer Format (10000 = 100%)
14 | 8 | Molar Analysis - CO2 | 402215 | Scaled Integer Format (10000 = 100%)
15 | 8 | Molar Analysis - C2 | 402216 | Scaled Integer Format (10000 = 100%)
16 | 8 | Molar Analysis - C3 | 402217 | Scaled Integer Format (10000 = 100%)
17 | 8 | Molar Analysis - H2O | 402218 | Scaled Integer Format (10000 = 100%)
18 | 8 | Molar Analysis - H2S | 402219 | Scaled Integer Format (10000 = 100%)
19 | 8 | Molar Analysis - H2 | 402220 | Scaled Integer Format (10000 = 100%)
20 | 8 | Molar Analysis - CO | 402221 | Scaled Integer Format (10000 = 100%)
21 | 8 | Molar Analysis - O2 | 402222 | Scaled Integer Format (10000 = 100%)
22 | 8 | Molar Analysis - iC4 | 402223 | Scaled Integer Format (10000 = 100%)
23 | 8 | Molar Analysis - C4 | 402224 | Scaled Integer Format (10000 = 100%)
24 | 8 | Molar Analysis - iC5 | 402225 | Scaled Integer Format (10000 = 100%)
25 | 8 | Molar Analysis - C5 | 402226 | Scaled Integer Format (10000 = 100%)
26 | 8 | Molar Analysis - C6 | 402227 | Scaled Integer Format (10000 = 100%)
27 | 8 | Molar Analysis - C7 | 402228 | Scaled Integer Format (10000 = 100%)
28 | 8 | Molar Analysis - C8 | 402229 | Scaled Integer Format (10000 = 100%)
29 | 8 | Molar Analysis - C9 | 402230 | Scaled Integer Format (10000 = 100%)
30 | 8 | Molar Analysis - C10 | 402231 | Scaled Integer Format (10000 = 100%)
31 | 8 | Molar Analysis - He | 402232 | Scaled Integer Format (10000 = 100%)
32 | 8 | Molar Analysis - Ar | 402233 | Scaled Integer Format (10000 = 100%)
33 | 8 | Molar Analysis - C5 (neo-p) | 402234 | Scaled Integer Format (10000 = 100%)
34 | 8 | Molar Analysis - Ux | 402235 | Scaled Integer Format (10000 = 100%)
35 | 8 | Molar Analysis - Uy | 402236 | Scaled Integer Format (10000 = 100%)
36 | 8 | Meter Signals - Reserved | 402237
37 | 8 | Meter Signals - Reserved | 402238
38 | 8 | Meter Signals - Reserved | 402239
39 | 8 | Meter Signals - Reserved | 402240
40 | 8 | Meter Signals - Reset Acc 1 | 402241
41 | 8 | Meter Signals - Reset Acc 2 | 402242
42 | 8 | Meter Signals - Reset Acc 3 | 402243
43 | 8 | Meter Signals - Reset Acc 4 | 402244
44 | 8 | Write Daily Archive | 402245
45 | 8 | Write Hourly Archive | 402246
46 | 8 | Meter Signals - Reserved | 402247
47 | 8 | Meter Signals - Reserved | 402248
48 | 8 | Meter Signals - Reserved | 402249
49 | 8 | Meter Signals - Reserved | 402250
50 | 8 | Meter Signals - Reserved | 402251
51 | 8 | Meter Signals - Reserved | 402252
52 | 8 | Analysis is Present | 402253
53 | 8 | Meter Archive Record Fetch | 402254 | (=0 signal not present)
54 | 8 | Meter Archive Record Age | 402255 | (=0 current)
55 | 8 | Meter Archive File Select | 402256 | (=0 daily, 1=hourly)
Meter 9 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Meter Disable | 402401
1 | 9 | Reserved | 402402
2 | 9 | Temperature | 402403 | Floating Point Format
3 | 9 | Temperature | 402404 | Floating Point Format
4 | 9 | Pressure | 402405 | Floating Point Format
5 | 9 | Pressure | 402406 | Floating Point Format
6 | 9 | Pulse Count | 402407 | Long Integer Format
7 | 9 | Pulse Count | 402408 | Long Integer Format
8 | 9 | Reserved | 402409
9 | 9 | Reserved | 402410
10 | 9 | Pulse Frequency | 402411 | Floating Point Format
11 | 9 | Pulse Frequency | 402412 | Floating Point Format
12 | 9 | Molar Analysis - C1 | 402413 | Scaled Integer Format (10000 = 100%)
13 | 9 | Molar Analysis - N2 | 402414 | Scaled Integer Format (10000 = 100%)
14 | 9 | Molar Analysis - CO2 | 402415 | Scaled Integer Format (10000 = 100%)
15 | 9 | Molar Analysis - C2 | 402416 | Scaled Integer Format (10000 = 100%)
16 | 9 | Molar Analysis - C3 | 402417 | Scaled Integer Format (10000 = 100%)
17 | 9 | Molar Analysis - H2O | 402418 | Scaled Integer Format (10000 = 100%)
18 | 9 | Molar Analysis - H2S | 402419 | Scaled Integer Format (10000 = 100%)
19 | 9 | Molar Analysis - H2 | 402420 | Scaled Integer Format (10000 = 100%)
20 | 9 | Molar Analysis - CO | 402421 | Scaled Integer Format (10000 = 100%)
21 | 9 | Molar Analysis - O2 | 402422 | Scaled Integer Format (10000 = 100%)
22 | 9 | Molar Analysis - iC4 | 402423 | Scaled Integer Format (10000 = 100%)
23 | 9 | Molar Analysis - C4 | 402424 | Scaled Integer Format (10000 = 100%)
24 | 9 | Molar Analysis - iC5 | 402425 | Scaled Integer Format (10000 = 100%)
25 | 9 | Molar Analysis - C5 | 402426 | Scaled Integer Format (10000 = 100%)
26 | 9 | Molar Analysis - C6 | 402427 | Scaled Integer Format (10000 = 100%)
27 | 9 | Molar Analysis - C7 | 402428 | Scaled Integer Format (10000 = 100%)
28 | 9 | Molar Analysis - C8 | 402429 | Scaled Integer Format (10000 = 100%)
29 | 9 | Molar Analysis - C9 | 402430 | Scaled Integer Format (10000 = 100%)
30 | 9 | Molar Analysis - C10 | 402431 | Scaled Integer Format (10000 = 100%)
31 | 9 | Molar Analysis - He | 402432 | Scaled Integer Format (10000 = 100%)
32 | 9 | Molar Analysis - Ar | 402433 | Scaled Integer Format (10000 = 100%)
33 | 9 | Molar Analysis - C5 (neo-p) | 402434 | Scaled Integer Format (10000 = 100%)
34 | 9 | Molar Analysis - Ux | 402435 | Scaled Integer Format (10000 = 100%)
35 | 9 | Molar Analysis - Uy | 402436 | Scaled Integer Format (10000 = 100%)
36 | 9 | Meter Signals - Reserved | 402437
37 | 9 | Meter Signals - Reserved | 402438
38 | 9 | Meter Signals - Reserved | 402439
39 | 9 | Meter Signals - Reserved | 402440
40 | 9 | Meter Signals - Reset Acc 1 | 402441
41 | 9 | Meter Signals - Reset Acc 2 | 402442
42 | 9 | Meter Signals - Reset Acc 3 | 402443
43 | 9 | Meter Signals - Reset Acc 4 | 402444
44 | 9 | Write Daily Archive | 402445
45 | 9 | Write Hourly Archive | 402446
46 | 9 | Meter Signals - Reserved | 402447
47 | 9 | Meter Signals - Reserved | 402448
48 | 9 | Meter Signals - Reserved | 402449
49 | 9 | Meter Signals - Reserved | 402450
50 | 9 | Meter Signals - Reserved | 402451
51 | 9 | Meter Signals - Reserved | 402452
52 | 9 | Analysis is Present | 402453
53 | 9 | Meter Archive Record Fetch | 402454 | (=0 signal not present)
54 | 9 | Meter Archive Record Age | 402455 | (=0 current)
55 | 9 | Meter Archive File Select | 402456 | (=0 daily, 1=hourly)
Meter 10 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Meter Disable | 402601
1 | 10 | Reserved | 402602
2 | 10 | Temperature | 402603 | Floating Point Format
3 | 10 | Temperature | 402604 | Floating Point Format
4 | 10 | Pressure | 402605 | Floating Point Format
5 | 10 | Pressure | 402606 | Floating Point Format
6 | 10 | Pulse Count | 402607 | Long Integer Format
7 | 10 | Pulse Count | 402608 | Long Integer Format
8 | 10 | Reserved | 402609
9 | 10 | Reserved | 402610
10 | 10 | Pulse Frequency | 402611 | Floating Point Format
11 | 10 | Pulse Frequency | 402612 | Floating Point Format
12 | 10 | Molar Analysis - C1 | 402613 | Scaled Integer Format (10000 = 100%)
13 | 10 | Molar Analysis - N2 | 402614 | Scaled Integer Format (10000 = 100%)
14 | 10 | Molar Analysis - CO2 | 402615 | Scaled Integer Format (10000 = 100%)
15 | 10 | Molar Analysis - C2 | 402616 | Scaled Integer Format (10000 = 100%)
16 | 10 | Molar Analysis - C3 | 402617 | Scaled Integer Format (10000 = 100%)
17 | 10 | Molar Analysis - H2O | 402618 | Scaled Integer Format (10000 = 100%)
18 | 10 | Molar Analysis - H2S | 402619 | Scaled Integer Format (10000 = 100%)
19 | 10 | Molar Analysis - H2 | 402620 | Scaled Integer Format (10000 = 100%)
20 | 10 | Molar Analysis - CO | 402621 | Scaled Integer Format (10000 = 100%)
21 | 10 | Molar Analysis - O2 | 402622 | Scaled Integer Format (10000 = 100%)
22 | 10 | Molar Analysis - iC4 | 402623 | Scaled Integer Format (10000 = 100%)
23 | 10 | Molar Analysis - C4 | 402624 | Scaled Integer Format (10000 = 100%)
24 | 10 | Molar Analysis - iC5 | 402625 | Scaled Integer Format (10000 = 100%)
25 | 10 | Molar Analysis - C5 | 402626 | Scaled Integer Format (10000 = 100%)
26 | 10 | Molar Analysis - C6 | 402627 | Scaled Integer Format (10000 = 100%)
27 | 10 | Molar Analysis - C7 | 402628 | Scaled Integer Format (10000 = 100%)
28 | 10 | Molar Analysis - C8 | 402629 | Scaled Integer Format (10000 = 100%)
29 | 10 | Molar Analysis - C9 | 402630 | Scaled Integer Format (10000 = 100%)
30 | 10 | Molar Analysis - C10 | 402631 | Scaled Integer Format (10000 = 100%)
31 | 10 | Molar Analysis - He | 402632 | Scaled Integer Format (10000 = 100%)
32 | 10 | Molar Analysis - Ar | 402633 | Scaled Integer Format (10000 = 100%)
33 | 10 | Molar Analysis - C5 (neo-p) | 402634 | Scaled Integer Format (10000 = 100%)
34 | 10 | Molar Analysis - Ux | 402635 | Scaled Integer Format (10000 = 100%)
35 | 10 | Molar Analysis - Uy | 402636 | Scaled Integer Format (10000 = 100%)
36 | 10 | Meter Signals - Reserved | 402637
37 | 10 | Meter Signals - Reserved | 402638
38 | 10 | Meter Signals - Reserved | 402639
39 | 10 | Meter Signals - Reserved | 402640
40 | 10 | Meter Signals - Reset Acc 1 | 402641
41 | 10 | Meter Signals - Reset Acc 2 | 402642
42 | 10 | Meter Signals - Reset Acc 3 | 402643
43 | 10 | Meter Signals - Reset Acc 4 | 402644
44 | 10 | Write Daily Archive | 402645
45 | 10 | Write Hourly Archive | 402646
46 | 10 | Meter Signals - Reserved | 402647
47 | 10 | Meter Signals - Reserved | 402648
48 | 10 | Meter Signals - Reserved | 402649
49 | 10 | Meter Signals - Reserved | 402650
50 | 10 | Meter Signals - Reserved | 402651
51 | 10 | Meter Signals - Reserved | 402652
52 | 10 | Analysis is Present | 402653
53 | 10 | Meter Archive Record Fetch | 402654 | (=0 signal not present)
54 | 10 | Meter Archive Record Age | 402655 | (=0 current)
55 | 10 | Meter Archive File Select | 402656 | (=0 daily, 1=hourly)
Meter 11 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Meter Disable | 402801
1 | 11 | Reserved | 402802
2 | 11 | Temperature | 402803 | Floating Point Format
3 | 11 | Temperature | 402804 | Floating Point Format
4 | 11 | Pressure | 402805 | Floating Point Format
5 | 11 | Pressure | 402806 | Floating Point Format
6 | 11 | Pulse Count | 402807 | Long Integer Format
7 | 11 | Pulse Count | 402808 | Long Integer Format
8 | 11 | Reserved | 402809
9 | 11 | Reserved | 402810
10 | 11 | Pulse Frequency | 402811 | Floating Point Format
11 | 11 | Pulse Frequency | 402812 | Floating Point Format
12 | 11 | Molar Analysis - C1 | 402813 | Scaled Integer Format (10000 = 100%)
13 | 11 | Molar Analysis - N2 | 402814 | Scaled Integer Format (10000 = 100%)
14 | 11 | Molar Analysis - CO2 | 402815 | Scaled Integer Format (10000 = 100%)
15 | 11 | Molar Analysis - C2 | 402816 | Scaled Integer Format (10000 = 100%)
16 | 11 | Molar Analysis - C3 | 402817 | Scaled Integer Format (10000 = 100%)
17 | 11 | Molar Analysis - H2O | 402818 | Scaled Integer Format (10000 = 100%)
18 | 11 | Molar Analysis - H2S | 402819 | Scaled Integer Format (10000 = 100%)
19 | 11 | Molar Analysis - H2 | 402820 | Scaled Integer Format (10000 = 100%)
20 | 11 | Molar Analysis - CO | 402821 | Scaled Integer Format (10000 = 100%)
21 | 11 | Molar Analysis - O2 | 402822 | Scaled Integer Format (10000 = 100%)
22 | 11 | Molar Analysis - iC4 | 402823 | Scaled Integer Format (10000 = 100%)
23 | 11 | Molar Analysis - C4 | 402824 | Scaled Integer Format (10000 = 100%)
24 | 11 | Molar Analysis - iC5 | 402825 | Scaled Integer Format (10000 = 100%)
25 | 11 | Molar Analysis - C5 | 402826 | Scaled Integer Format (10000 = 100%)
26 | 11 | Molar Analysis - C6 | 402827 | Scaled Integer Format (10000 = 100%)
27 | 11 | Molar Analysis - C7 | 402828 | Scaled Integer Format (10000 = 100%)
28 | 11 | Molar Analysis - C8 | 402829 | Scaled Integer Format (10000 = 100%)
29 | 11 | Molar Analysis - C9 | 402830 | Scaled Integer Format (10000 = 100%)
30 | 11 | Molar Analysis - C10 | 402831 | Scaled Integer Format (10000 = 100%)
31 | 11 | Molar Analysis - He | 402832 | Scaled Integer Format (10000 = 100%)
32 | 11 | Molar Analysis - Ar | 402833 | Scaled Integer Format (10000 = 100%)
33 | 11 | Molar Analysis - C5 (neo-p) | 402834 | Scaled Integer Format (10000 = 100%)
34 | 11 | Molar Analysis - Ux | 402835 | Scaled Integer Format (10000 = 100%)
35 | 11 | Molar Analysis - Uy | 402836 | Scaled Integer Format (10000 = 100%)
36 | 11 | Meter Signals - Reserved | 402837
37 | 11 | Meter Signals - Reserved | 402838
38 | 11 | Meter Signals - Reserved | 402839
39 | 11 | Meter Signals - Reserved | 402840
40 | 11 | Meter Signals - Reset Acc 1 | 402841
41 | 11 | Meter Signals - Reset Acc 2 | 402842
42 | 11 | Meter Signals - Reset Acc 3 | 402843
43 | 11 | Meter Signals - Reset Acc 4 | 402844
44 | 11 | Write Daily Archive | 402845
45 | 11 | Write Hourly Archive | 402846
46 | 11 | Meter Signals - Reserved | 402847
47 | 11 | Meter Signals - Reserved | 402848
48 | 11 | Meter Signals - Reserved | 402849
49 | 11 | Meter Signals - Reserved | 402850
50 | 11 | Meter Signals - Reserved | 402851
51 | 11 | Meter Signals - Reserved | 402852
52 | 11 | Analysis is Present | 402853
53 | 11 | Meter Archive Record Fetch | 402854 | (=0 signal not present)
54 | 11 | Meter Archive Record Age | 402855 | (=0 current)
55 | 11 | Meter Archive File Select | 402856 | (=0 daily, 1=hourly)
Meter 12 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Meter Disable | 403001
1 | 12 | Reserved | 403002
2 | 12 | Temperature | 403003 | Floating Point Format
3 | 12 | Temperature | 403004 | Floating Point Format
4 | 12 | Pressure | 403005 | Floating Point Format
5 | 12 | Pressure | 403006 | Floating Point Format
6 | 12 | Pulse Count | 403007 | Long Integer Format
7 | 12 | Pulse Count | 403008 | Long Integer Format
8 | 12 | Reserved | 403009
9 | 12 | Reserved | 403010
10 | 12 | Pulse Frequency | 403011 | Floating Point Format
11 | 12 | Pulse Frequency | 403012 | Floating Point Format
12 | 12 | Molar Analysis - C1 | 403013 | Scaled Integer Format (10000 = 100%)
13 | 12 | Molar Analysis - N2 | 403014 | Scaled Integer Format (10000 = 100%)
14 | 12 | Molar Analysis - CO2 | 403015 | Scaled Integer Format (10000 = 100%)
15 | 12 | Molar Analysis - C2 | 403016 | Scaled Integer Format (10000 = 100%)
16 | 12 | Molar Analysis - C3 | 403017 | Scaled Integer Format (10000 = 100%)
17 | 12 | Molar Analysis - H2O | 403018 | Scaled Integer Format (10000 = 100%)
18 | 12 | Molar Analysis - H2S | 403019 | Scaled Integer Format (10000 = 100%)
19 | 12 | Molar Analysis - H2 | 403020 | Scaled Integer Format (10000 = 100%)
20 | 12 | Molar Analysis - CO | 403021 | Scaled Integer Format (10000 = 100%)
21 | 12 | Molar Analysis - O2 | 403022 | Scaled Integer Format (10000 = 100%)
22 | 12 | Molar Analysis - iC4 | 403023 | Scaled Integer Format (10000 = 100%)
23 | 12 | Molar Analysis - C4 | 403024 | Scaled Integer Format (10000 = 100%)
24 | 12 | Molar Analysis - iC5 | 403025 | Scaled Integer Format (10000 = 100%)
25 | 12 | Molar Analysis - C5 | 403026 | Scaled Integer Format (10000 = 100%)
26 | 12 | Molar Analysis - C6 | 403027 | Scaled Integer Format (10000 = 100%)
27 | 12 | Molar Analysis - C7 | 403028 | Scaled Integer Format (10000 = 100%)
28 | 12 | Molar Analysis - C8 | 403029 | Scaled Integer Format (10000 = 100%)
29 | 12 | Molar Analysis - C9 | 403030 | Scaled Integer Format (10000 = 100%)
30 | 12 | Molar Analysis - C10 | 403031 | Scaled Integer Format (10000 = 100%)
31 | 12 | Molar Analysis - He | 403032 | Scaled Integer Format (10000 = 100%)
32 | 12 | Molar Analysis - Ar | 403033 | Scaled Integer Format (10000 = 100%)
33 | 12 | Molar Analysis - C5 (neo-p) | 403034 | Scaled Integer Format (10000 = 100%)
34 | 12 | Molar Analysis - Ux | 403035 | Scaled Integer Format (10000 = 100%)
35 | 12 | Molar Analysis - Uy | 403036 | Scaled Integer Format (10000 = 100%)
36 | 12 | Meter Signals - Reserved | 403037
37 | 12 | Meter Signals - Reserved | 403038
38 | 12 | Meter Signals - Reserved | 403039
39 | 12 | Meter Signals - Reserved | 403040
40 | 12 | Meter Signals - Reset Acc 1 | 403041
41 | 12 | Meter Signals - Reset Acc 2 | 403042
42 | 12 | Meter Signals - Reset Acc 3 | 403043
43 | 12 | Meter Signals - Reset Acc 4 | 403044
44 | 12 | Write Daily Archive | 403045
45 | 12 | Write Hourly Archive | 403046
46 | 12 | Meter Signals - Reserved | 403047
47 | 12 | Meter Signals - Reserved | 403048
48 | 12 | Meter Signals - Reserved | 403049
49 | 12 | Meter Signals - Reserved | 403050
50 | 12 | Meter Signals - Reserved | 403051
51 | 12 | Meter Signals - Reserved | 403052
52 | 12 | Analysis is Present | 403053
53 | 12 | Meter Archive Record Fetch | 403054 | (=0 signal not present)
54 | 12 | Meter Archive Record Age | 403055 | (=0 current)
55 | 12 | Meter Archive File Select | 403056 | (=0 daily, 1=hourly)
Meter 13 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Meter Disable | 403201
1 | 13 | Reserved | 403202
2 | 13 | Temperature | 403203 | Floating Point Format
3 | 13 | Temperature | 403204 | Floating Point Format
4 | 13 | Pressure | 403205 | Floating Point Format
5 | 13 | Pressure | 403206 | Floating Point Format
6 | 13 | Pulse Count | 403207 | Long Integer Format
7 | 13 | Pulse Count | 403208 | Long Integer Format
8 | 13 | Reserved | 403209
9 | 13 | Reserved | 403210
10 | 13 | Pulse Frequency | 403211 | Floating Point Format
11 | 13 | Pulse Frequency | 403212 | Floating Point Format
12 | 13 | Molar Analysis - C1 | 403213 | Scaled Integer Format (10000 = 100%)
13 | 13 | Molar Analysis - N2 | 403214 | Scaled Integer Format (10000 = 100%)
14 | 13 | Molar Analysis - CO2 | 403215 | Scaled Integer Format (10000 = 100%)
15 | 13 | Molar Analysis - C2 | 403216 | Scaled Integer Format (10000 = 100%)
16 | 13 | Molar Analysis - C3 | 403217 | Scaled Integer Format (10000 = 100%)
17 | 13 | Molar Analysis - H2O | 403218 | Scaled Integer Format (10000 = 100%)
18 | 13 | Molar Analysis - H2S | 403219 | Scaled Integer Format (10000 = 100%)
19 | 13 | Molar Analysis - H2 | 403220 | Scaled Integer Format (10000 = 100%)
20 | 13 | Molar Analysis - CO | 403221 | Scaled Integer Format (10000 = 100%)
21 | 13 | Molar Analysis - O2 | 403222 | Scaled Integer Format (10000 = 100%)
22 | 13 | Molar Analysis - iC4 | 403223 | Scaled Integer Format (10000 = 100%)
23 | 13 | Molar Analysis - C4 | 403224 | Scaled Integer Format (10000 = 100%)
24 | 13 | Molar Analysis - iC5 | 403225 | Scaled Integer Format (10000 = 100%)
25 | 13 | Molar Analysis - C5 | 403226 | Scaled Integer Format (10000 = 100%)
26 | 13 | Molar Analysis - C6 | 403227 | Scaled Integer Format (10000 = 100%)
27 | 13 | Molar Analysis - C7 | 403228 | Scaled Integer Format (10000 = 100%)
28 | 13 | Molar Analysis - C8 | 403229 | Scaled Integer Format (10000 = 100%)
29 | 13 | Molar Analysis - C9 | 403230 | Scaled Integer Format (10000 = 100%)
30 | 13 | Molar Analysis - C10 | 403231 | Scaled Integer Format (10000 = 100%)
31 | 13 | Molar Analysis - He | 403232 | Scaled Integer Format (10000 = 100%)
32 | 13 | Molar Analysis - Ar | 403233 | Scaled Integer Format (10000 = 100%)
33 | 13 | Molar Analysis - C5 (neo-p) | 403234 | Scaled Integer Format (10000 = 100%)
34 | 13 | Molar Analysis - Ux | 403235 | Scaled Integer Format (10000 = 100%)
35 | 13 | Molar Analysis - Uy | 403236 | Scaled Integer Format (10000 = 100%)
36 | 13 | Meter Signals - Reserved | 403237
37 | 13 | Meter Signals - Reserved | 403238
38 | 13 | Meter Signals - Reserved | 403239
39 | 13 | Meter Signals - Reserved | 403240
40 | 13 | Meter Signals - Reset Acc 1 | 403241
41 | 13 | Meter Signals - Reset Acc 2 | 403242
42 | 13 | Meter Signals - Reset Acc 3 | 403243
43 | 13 | Meter Signals - Reset Acc 4 | 403244
44 | 13 | Write Daily Archive | 403245
45 | 13 | Write Hourly Archive | 403246
46 | 13 | Meter Signals - Reserved | 403247
47 | 13 | Meter Signals - Reserved | 403248
48 | 13 | Meter Signals - Reserved | 403249
49 | 13 | Meter Signals - Reserved | 403250
50 | 13 | Meter Signals - Reserved | 403251
51 | 13 | Meter Signals - Reserved | 403252
52 | 13 | Analysis is Present | 403253
53 | 13 | Meter Archive Record Fetch | 403254 | (=0 signal not present)
54 | 13 | Meter Archive Record Age | 403255 | (=0 current)
55 | 13 | Meter Archive File Select | 403256 | (=0 daily, 1=hourly)
Meter 14 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Meter Disable | 403401
1 | 14 | Reserved | 403402
2 | 14 | Temperature | 403403 | Floating Point Format
3 | 14 | Temperature | 403404 | Floating Point Format
4 | 14 | Pressure | 403405 | Floating Point Format
5 | 14 | Pressure | 403406 | Floating Point Format
6 | 14 | Pulse Count | 403407 | Long Integer Format
7 | 14 | Pulse Count | 403408 | Long Integer Format
8 | 14 | Reserved | 403409
9 | 14 | Reserved | 403410
10 | 14 | Pulse Frequency | 403411 | Floating Point Format
11 | 14 | Pulse Frequency | 403412 | Floating Point Format
12 | 14 | Molar Analysis - C1 | 403413 | Scaled Integer Format (10000 = 100%)
13 | 14 | Molar Analysis - N2 | 403414 | Scaled Integer Format (10000 = 100%)
14 | 14 | Molar Analysis - CO2 | 403415 | Scaled Integer Format (10000 = 100%)
15 | 14 | Molar Analysis - C2 | 403416 | Scaled Integer Format (10000 = 100%)
16 | 14 | Molar Analysis - C3 | 403417 | Scaled Integer Format (10000 = 100%)
17 | 14 | Molar Analysis - H2O | 403418 | Scaled Integer Format (10000 = 100%)
18 | 14 | Molar Analysis - H2S | 403419 | Scaled Integer Format (10000 = 100%)
19 | 14 | Molar Analysis - H2 | 403420 | Scaled Integer Format (10000 = 100%)
20 | 14 | Molar Analysis - CO | 403421 | Scaled Integer Format (10000 = 100%)
21 | 14 | Molar Analysis - O2 | 403422 | Scaled Integer Format (10000 = 100%)
22 | 14 | Molar Analysis - iC4 | 403423 | Scaled Integer Format (10000 = 100%)
23 | 14 | Molar Analysis - C4 | 403424 | Scaled Integer Format (10000 = 100%)
24 | 14 | Molar Analysis - iC5 | 403425 | Scaled Integer Format (10000 = 100%)
25 | 14 | Molar Analysis - C5 | 403426 | Scaled Integer Format (10000 = 100%)
26 | 14 | Molar Analysis - C6 | 403427 | Scaled Integer Format (10000 = 100%)
27 | 14 | Molar Analysis - C7 | 403428 | Scaled Integer Format (10000 = 100%)
28 | 14 | Molar Analysis - C8 | 403429 | Scaled Integer Format (10000 = 100%)
29 | 14 | Molar Analysis - C9 | 403430 | Scaled Integer Format (10000 = 100%)
30 | 14 | Molar Analysis - C10 | 403431 | Scaled Integer Format (10000 = 100%)
31 | 14 | Molar Analysis - He | 403432 | Scaled Integer Format (10000 = 100%)
32 | 14 | Molar Analysis - Ar | 403433 | Scaled Integer Format (10000 = 100%)
33 | 14 | Molar Analysis - C5 (neo-p) | 403434 | Scaled Integer Format (10000 = 100%)
34 | 14 | Molar Analysis - Ux | 403435 | Scaled Integer Format (10000 = 100%)
35 | 14 | Molar Analysis - Uy | 403436 | Scaled Integer Format (10000 = 100%)
36 | 14 | Meter Signals - Reserved | 403437
37 | 14 | Meter Signals - Reserved | 403438
38 | 14 | Meter Signals - Reserved | 403439
39 | 14 | Meter Signals - Reserved | 403440
40 | 14 | Meter Signals - Reset Acc 1 | 403441
41 | 14 | Meter Signals - Reset Acc 2 | 403442
42 | 14 | Meter Signals - Reset Acc 3 | 403443
43 | 14 | Meter Signals - Reset Acc 4 | 403444
44 | 14 | Write Daily Archive | 403445
45 | 14 | Write Hourly Archive | 403446
46 | 14 | Meter Signals - Reserved | 403447
47 | 14 | Meter Signals - Reserved | 403448
48 | 14 | Meter Signals - Reserved | 403449
49 | 14 | Meter Signals - Reserved | 403450
50 | 14 | Meter Signals - Reserved | 403451
51 | 14 | Meter Signals - Reserved | 403452
52 | 14 | Analysis is Present | 403453
53 | 14 | Meter Archive Record Fetch | 403454 | (=0 signal not present)
54 | 14 | Meter Archive Record Age | 403455 | (=0 current)
55 | 14 | Meter Archive File Select | 403456 | (=0 daily, 1=hourly)
Meter 15 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Meter Disable | 403601
1 | 15 | Reserved | 403602
2 | 15 | Temperature | 403603 | Floating Point Format
3 | 15 | Temperature | 403604 | Floating Point Format
4 | 15 | Pressure | 403605 | Floating Point Format
5 | 15 | Pressure | 403606 | Floating Point Format
6 | 15 | Pulse Count | 403607 | Long Integer Format
7 | 15 | Pulse Count | 403608 | Long Integer Format
8 | 15 | Reserved | 403609
9 | 15 | Reserved | 403610
10 | 15 | Pulse Frequency | 403611 | Floating Point Format
11 | 15 | Pulse Frequency | 403612 | Floating Point Format
12 | 15 | Molar Analysis - C1 | 403613 | Scaled Integer Format (10000 = 100%)
13 | 15 | Molar Analysis - N2 | 403614 | Scaled Integer Format (10000 = 100%)
14 | 15 | Molar Analysis - CO2 | 403615 | Scaled Integer Format (10000 = 100%)
15 | 15 | Molar Analysis - C2 | 403616 | Scaled Integer Format (10000 = 100%)
16 | 15 | Molar Analysis - C3 | 403617 | Scaled Integer Format (10000 = 100%)
17 | 15 | Molar Analysis - H2O | 403618 | Scaled Integer Format (10000 = 100%)
18 | 15 | Molar Analysis - H2S | 403619 | Scaled Integer Format (10000 = 100%)
19 | 15 | Molar Analysis - H2 | 403620 | Scaled Integer Format (10000 = 100%)
20 | 15 | Molar Analysis - CO | 403621 | Scaled Integer Format (10000 = 100%)
21 | 15 | Molar Analysis - O2 | 403622 | Scaled Integer Format (10000 = 100%)
22 | 15 | Molar Analysis - iC4 | 403623 | Scaled Integer Format (10000 = 100%)
23 | 15 | Molar Analysis - C4 | 403624 | Scaled Integer Format (10000 = 100%)
24 | 15 | Molar Analysis - iC5 | 403625 | Scaled Integer Format (10000 = 100%)
25 | 15 | Molar Analysis - C5 | 403626 | Scaled Integer Format (10000 = 100%)
26 | 15 | Molar Analysis - C6 | 403627 | Scaled Integer Format (10000 = 100%)
27 | 15 | Molar Analysis - C7 | 403628 | Scaled Integer Format (10000 = 100%)
28 | 15 | Molar Analysis - C8 | 403629 | Scaled Integer Format (10000 = 100%)
29 | 15 | Molar Analysis - C9 | 403630 | Scaled Integer Format (10000 = 100%)
30 | 15 | Molar Analysis - C10 | 403631 | Scaled Integer Format (10000 = 100%)
31 | 15 | Molar Analysis - He | 403632 | Scaled Integer Format (10000 = 100%)
32 | 15 | Molar Analysis - Ar | 403633 | Scaled Integer Format (10000 = 100%)
33 | 15 | Molar Analysis - C5 (neo-p) | 403634 | Scaled Integer Format (10000 = 100%)
34 | 15 | Molar Analysis - Ux | 403635 | Scaled Integer Format (10000 = 100%)
35 | 15 | Molar Analysis - Uy | 403636 | Scaled Integer Format (10000 = 100%)
36 | 15 | Meter Signals - Reserved | 403637
37 | 15 | Meter Signals - Reserved | 403638
38 | 15 | Meter Signals - Reserved | 403639
39 | 15 | Meter Signals - Reserved | 403640
40 | 15 | Meter Signals - Reset Acc 1 | 403641
41 | 15 | Meter Signals - Reset Acc 2 | 403642
42 | 15 | Meter Signals - Reset Acc 3 | 403643
43 | 15 | Meter Signals - Reset Acc 4 | 403644
44 | 15 | Write Daily Archive | 403645
45 | 15 | Write Hourly Archive | 403646
46 | 15 | Meter Signals - Reserved | 403647
47 | 15 | Meter Signals - Reserved | 403648
48 | 15 | Meter Signals - Reserved | 403649
49 | 15 | Meter Signals - Reserved | 403650
50 | 15 | Meter Signals - Reserved | 403651
51 | 15 | Meter Signals - Reserved | 403652
52 | 15 | Analysis is Present | 403653
53 | 15 | Meter Archive Record Fetch | 403654 | (=0 signal not present)
54 | 15 | Meter Archive Record Age | 403655 | (=0 current)
55 | 15 | Meter Archive File Select | 403656 | (=0 daily, 1=hourly)
Meter 16 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Meter Disable | 403801
1 | 16 | Reserved | 403802
2 | 16 | Temperature | 403803 | Floating Point Format
3 | 16 | Temperature | 403804 | Floating Point Format
4 | 16 | Pressure | 403805 | Floating Point Format
5 | 16 | Pressure | 403806 | Floating Point Format
6 | 16 | Pulse Count | 403807 | Long Integer Format
7 | 16 | Pulse Count | 403808 | Long Integer Format
8 | 16 | Reserved | 403809
9 | 16 | Reserved | 403810
10 | 16 | Pulse Frequency | 403811 | Floating Point Format
11 | 16 | Pulse Frequency | 403812 | Floating Point Format
12 | 16 | Molar Analysis - C1 | 403813 | Scaled Integer Format (10000 = 100%)
13 | 16 | Molar Analysis - N2 | 403814 | Scaled Integer Format (10000 = 100%)
14 | 16 | Molar Analysis - CO2 | 403815 | Scaled Integer Format (10000 = 100%)
15 | 16 | Molar Analysis - C2 | 403816 | Scaled Integer Format (10000 = 100%)
16 | 16 | Molar Analysis - C3 | 403817 | Scaled Integer Format (10000 = 100%)
17 | 16 | Molar Analysis - H2O | 403818 | Scaled Integer Format (10000 = 100%)
18 | 16 | Molar Analysis - H2S | 403819 | Scaled Integer Format (10000 = 100%)
19 | 16 | Molar Analysis - H2 | 403820 | Scaled Integer Format (10000 = 100%)
20 | 16 | Molar Analysis - CO | 403821 | Scaled Integer Format (10000 = 100%)
21 | 16 | Molar Analysis - O2 | 403822 | Scaled Integer Format (10000 = 100%)
22 | 16 | Molar Analysis - iC4 | 403823 | Scaled Integer Format (10000 = 100%)
23 | 16 | Molar Analysis - C4 | 403824 | Scaled Integer Format (10000 = 100%)
24 | 16 | Molar Analysis - iC5 | 403825 | Scaled Integer Format (10000 = 100%)
25 | 16 | Molar Analysis - C5 | 403826 | Scaled Integer Format (10000 = 100%)
26 | 16 | Molar Analysis - C6 | 403827 | Scaled Integer Format (10000 = 100%)
27 | 16 | Molar Analysis - C7 | 403828 | Scaled Integer Format (10000 = 100%)
28 | 16 | Molar Analysis - C8 | 403829 | Scaled Integer Format (10000 = 100%)
29 | 16 | Molar Analysis - C9 | 403830 | Scaled Integer Format (10000 = 100%)
30 | 16 | Molar Analysis - C10 | 403831 | Scaled Integer Format (10000 = 100%)
31 | 16 | Molar Analysis - He | 403832 | Scaled Integer Format (10000 = 100%)
32 | 16 | Molar Analysis - Ar | 403833 | Scaled Integer Format (10000 = 100%)
33 | 16 | Molar Analysis - C5 (neo-p) | 403834 | Scaled Integer Format (10000 = 100%)
34 | 16 | Molar Analysis - Ux | 403835 | Scaled Integer Format (10000 = 100%)
35 | 16 | Molar Analysis - Uy | 403836 | Scaled Integer Format (10000 = 100%)
36 | 16 | Meter Signals - Reserved | 403837
37 | 16 | Meter Signals - Reserved | 403838
38 | 16 | Meter Signals - Reserved | 403839
39 | 16 | Meter Signals - Reserved | 403840
40 | 16 | Meter Signals - Reset Acc 1 | 403841
41 | 16 | Meter Signals - Reset Acc 2 | 403842
42 | 16 | Meter Signals - Reset Acc 3 | 403843
43 | 16 | Meter Signals - Reset Acc 4 | 403844
44 | 16 | Write Daily Archive | 403845
45 | 16 | Write Hourly Archive | 403846
46 | 16 | Meter Signals - Reserved | 403847
47 | 16 | Meter Signals - Reserved | 403848
48 | 16 | Meter Signals - Reserved | 403849
49 | 16 | Meter Signals - Reserved | 403850
50 | 16 | Meter Signals - Reserved | 403851
51 | 16 | Meter Signals - Reserved | 403852
52 | 16 | Analysis is Present | 403853
53 | 16 | Meter Archive Record Fetch | 403854 | (=0 signal not present)
54 | 16 | Meter Archive Record Age | 403855 | (=0 current)
55 | 16 | Meter Archive File Select | 403856 | (=0 daily, 1=hourly)

## Meter Results - Pulse & Gas
Meter 1 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Scan Count: process input | 400901
1 | 1 | Scan Count: calculation | 400902
2 | 1 | Meter in Alarm | 400903 | 0=no alarm
3 | 1 | Reserved | 400904
4 | 1 | Net Accumulator | 400905 | Long Integer Format
5 | 1 | Net Accumulator | 400906 | Long Integer Format
6 | 1 | Net Flow Rate | 400907 | Floating Point Format
7 | 1 | Net Flow Rate | 400908 | Floating Point Format
8 | 1 | Gross Flow Rate | 400909 | Floating Point Format
9 | 1 | Gross Flow Rate | 400910 | Floating Point Format
10 | 1 | Fpv | 400911 | Floating Point Format
11 | 1 | Fpv | 400912 | Floating Point Format
12 | 1 | Cprime | 400913 | Floating Point Format
13 | 1 | Cprime | 400914 | Floating Point Format
14 | 1 | Reserved | 400915
15 | 1 | Reserved | 400916
16 | 1 | Reserved | 400917
17 | 1 | Reserved | 400918
18 | 1 | Reserved | 400919
19 | 1 | Reserved | 400920
20 | 1 | Reserved | 400921
21 | 1 | Reserved | 400922
22 | 1 | Reserved | 400923
23 | 1 | Reserved | 400924
24 | 1 | Reserved | 400925
25 | 1 | Reserved | 400926
26 | 1 | Reserved | 400927
27 | 1 | Reserved | 400928
28 | 1 | Reserved | 400929
29 | 1 | Reserved | 400930
30 | 1 | Reserved | 400931
31 | 1 | Reserved | 400932
32 | 1 | Reserved | 400933
33 | 1 | Reserved | 400934
34 | 1 | Reserved | 400935
35 | 1 | Reserved | 400936
36 | 1 | Reserved | 400937
37 | 1 | Reserved | 400938
Meter 2 Results Puse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Scan Count: process input | 401101
1 | 2 | Scan Count: calculation | 401102
2 | 2 | Meter in Alarm | 401103 | 0=no alarm
3 | 2 | Reserved | 401104
4 | 2 | Net Accumulator | 401105 | Long Integer Format
5 | 2 | Net Accumulator | 401106 | Long Integer Format
6 | 2 | Net Flow Rate | 401107 | Floating Point Format
7 | 2 | Net Flow Rate | 401108 | Floating Point Format
8 | 2 | Gross Flow Rate | 401109 | Floating Point Format
9 | 2 | Gross Flow Rate | 401110 | Floating Point Format
10 | 2 | Fpv | 401111 | Floating Point Format
11 | 2 | Fpv | 401112 | Floating Point Format
12 | 2 | Cprime | 401113 | Floating Point Format
13 | 2 | Cprime | 401114 | Floating Point Format
14 | 2 | Reserved | 401115
15 | 2 | Reserved | 401116
16 | 2 | Reserved | 401117
17 | 2 | Reserved | 401118
18 | 2 | Reserved | 401119
19 | 2 | Reserved | 401120
20 | 2 | Reserved | 401121
21 | 2 | Reserved | 401122
22 | 2 | Reserved | 401123
23 | 2 | Reserved | 401124
24 | 2 | Reserved | 401125
25 | 2 | Reserved | 401126
26 | 2 | Reserved | 401127
27 | 2 | Reserved | 401128
28 | 2 | Reserved | 401129
29 | 2 | Reserved | 401130
30 | 2 | Reserved | 401131
31 | 2 | Reserved | 401132
32 | 2 | Reserved | 401133
33 | 2 | Reserved | 401134
34 | 2 | Reserved | 401135
35 | 2 | Reserved | 401136
36 | 2 | Reserved | 401137
37 | 2 | Reserved | 401138
Meter 3 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Scan Count: process input | 401301
1 | 3 | Scan Count: calculation | 401302
2 | 3 | Meter in Alarm | 401303 | 0=no alarm
3 | 3 | Reserved | 401304
4 | 3 | Net Accumulator | 401305 | Long Integer Format
5 | 3 | Net Accumulator | 401306 | Long Integer Format
6 | 3 | Net Flow Rate | 401307 | Floating Point Format
7 | 3 | Net Flow Rate | 401308 | Floating Point Format
8 | 3 | Gross Flow Rate | 401309 | Floating Point Format
9 | 3 | Gross Flow Rate | 401310 | Floating Point Format
10 | 3 | Fpv | 401311 | Floating Point Format
11 | 3 | Fpv | 401312 | Floating Point Format
12 | 3 | Cprime | 401313 | Floating Point Format
13 | 3 | Cprime | 401314 | Floating Point Format
14 | 3 | Reserved | 401315
15 | 3 | Reserved | 401316
16 | 3 | Reserved | 401317
17 | 3 | Reserved | 401318
18 | 3 | Reserved | 401319
19 | 3 | Reserved | 401320
20 | 3 | Reserved | 401321
21 | 3 | Reserved | 401322
22 | 3 | Reserved | 401323
23 | 3 | Reserved | 401324
24 | 3 | Reserved | 401325
25 | 3 | Reserved | 401326
26 | 3 | Reserved | 401327
27 | 3 | Reserved | 401328
28 | 3 | Reserved | 401329
29 | 3 | Reserved | 401330
30 | 3 | Reserved | 401331
31 | 3 | Reserved | 401332
32 | 3 | Reserved | 401333
33 | 3 | Reserved | 401334
34 | 3 | Reserved | 401335
35 | 3 | Reserved | 401336
36 | 3 | Reserved | 401337
37 | 3 | Reserved | 401338
Meter 4 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Scan Count: process input | 401501
1 | 4 | Scan Count: calculation | 401502
2 | 4 | Meter in Alarm | 401503 | 0=no alarm
3 | 4 | Reserved | 401504
4 | 4 | Net Accumulator | 401505 | Long Integer Format
5 | 4 | Net Accumulator | 401506 | Long Integer Format
6 | 4 | Net Flow Rate | 401507 | Floating Point Format
7 | 4 | Net Flow Rate | 401508 | Floating Point Format
8 | 4 | Gross Flow Rate | 401509 | Floating Point Format
9 | 4 | Gross Flow Rate | 401510 | Floating Point Format
10 | 4 | Fpv | 401511 | Floating Point Format
11 | 4 | Fpv | 401512 | Floating Point Format
12 | 4 | Cprime | 401513 | Floating Point Format
13 | 4 | Cprime | 401514 | Floating Point Format
14 | 4 | Reserved | 401515
15 | 4 | Reserved | 401516
16 | 4 | Reserved | 401517
17 | 4 | Reserved | 401518
18 | 4 | Reserved | 401519
19 | 4 | Reserved | 401520
20 | 4 | Reserved | 401521
21 | 4 | Reserved | 401522
22 | 4 | Reserved | 401523
23 | 4 | Reserved | 401524
24 | 4 | Reserved | 401525
25 | 4 | Reserved | 401526
26 | 4 | Reserved | 401527
27 | 4 | Reserved | 401528
28 | 4 | Reserved | 401529
29 | 4 | Reserved | 401530
30 | 4 | Reserved | 401531
31 | 4 | Reserved | 401532
32 | 4 | Reserved | 401533
33 | 4 | Reserved | 401534
34 | 4 | Reserved | 401535
35 | 4 | Reserved | 401536
36 | 4 | Reserved | 401537
37 | 4 | Reserved | 401538
Meter 5 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Scan Count: process input | 401701
1 | 5 | Scan Count: calculation | 401702
2 | 5 | Meter in Alarm | 401703 | 0=no alarm
3 | 5 | Reserved | 401704
4 | 5 | Net Accumulator | 401705 | Long Integer Format
5 | 5 | Net Accumulator | 401706 | Long Integer Format
6 | 5 | Net Flow Rate | 401707 | Floating Point Format
7 | 5 | Net Flow Rate | 401708 | Floating Point Format
8 | 5 | Gross Flow Rate | 401709 | Floating Point Format
9 | 5 | Gross Flow Rate | 401710 | Floating Point Format
10 | 5 | Fpv | 401711 | Floating Point Format
11 | 5 | Fpv | 401712 | Floating Point Format
12 | 5 | Cprime | 401713 | Floating Point Format
13 | 5 | Cprime | 401714 | Floating Point Format
14 | 5 | Reserved | 401715
15 | 5 | Reserved | 401716
16 | 5 | Reserved | 401717
17 | 5 | Reserved | 401718
18 | 5 | Reserved | 401719
19 | 5 | Reserved | 401720
20 | 5 | Reserved | 401721
21 | 5 | Reserved | 401722
22 | 5 | Reserved | 401723
23 | 5 | Reserved | 401724
24 | 5 | Reserved | 401725
25 | 5 | Reserved | 401726
26 | 5 | Reserved | 401727
27 | 5 | Reserved | 401728
28 | 5 | Reserved | 401729
29 | 5 | Reserved | 401730
30 | 5 | Reserved | 401731
31 | 5 | Reserved | 401732
32 | 5 | Reserved | 401733
33 | 5 | Reserved | 401734
34 | 5 | Reserved | 401735
35 | 5 | Reserved | 401736
36 | 5 | Reserved | 401737
37 | 5 | Reserved | 401738
Meter 6 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Scan Count: process input | 401901
1 | 6 | Scan Count: calculation | 401902
2 | 6 | Meter in Alarm | 401903 | 0=no alarm
3 | 6 | Reserved | 401904
4 | 6 | Net Accumulator | 401905 | Long Integer Format
5 | 6 | Net Accumulator | 401906 | Long Integer Format
6 | 6 | Net Flow Rate | 401907 | Floating Point Format
7 | 6 | Net Flow Rate | 401908 | Floating Point Format
8 | 6 | Gross Flow Rate | 401909 | Floating Point Format
9 | 6 | Gross Flow Rate | 401910 | Floating Point Format
10 | 6 | Fpv | 401911 | Floating Point Format
11 | 6 | Fpv | 401912 | Floating Point Format
12 | 6 | Cprime | 401913 | Floating Point Format
13 | 6 | Cprime | 401914 | Floating Point Format
14 | 6 | Reserved | 401915
15 | 6 | Reserved | 401916
16 | 6 | Reserved | 401917
17 | 6 | Reserved | 401918
18 | 6 | Reserved | 401919
19 | 6 | Reserved | 401920
20 | 6 | Reserved | 401921
21 | 6 | Reserved | 401922
22 | 6 | Reserved | 401923
23 | 6 | Reserved | 401924
24 | 6 | Reserved | 401925
25 | 6 | Reserved | 401926
26 | 6 | Reserved | 401927
27 | 6 | Reserved | 401928
28 | 6 | Reserved | 401929
29 | 6 | Reserved | 401930
30 | 6 | Reserved | 401931
31 | 6 | Reserved | 401932
32 | 6 | Reserved | 401933
33 | 6 | Reserved | 401934
34 | 6 | Reserved | 401935
35 | 6 | Reserved | 401936
36 | 6 | Reserved | 401937
37 | 6 | Reserved | 401938
Meter 7 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Scan Count: process input | 402101
1 | 7 | Scan Count: calculation | 402102
2 | 7 | Meter in Alarm | 402103 | 0=no alarm
3 | 7 | Reserved | 402104
4 | 7 | Net Accumulator | 402105 | Long Integer Format
5 | 7 | Net Accumulator | 402106 | Long Integer Format
6 | 7 | Net Flow Rate | 402107 | Floating Point Format
7 | 7 | Net Flow Rate | 402108 | Floating Point Format
8 | 7 | Gross Flow Rate | 402109 | Floating Point Format
9 | 7 | Gross Flow Rate | 402110 | Floating Point Format
10 | 7 | Fpv | 402111 | Floating Point Format
11 | 7 | Fpv | 402112 | Floating Point Format
12 | 7 | Cprime | 402113 | Floating Point Format
13 | 7 | Cprime | 402114 | Floating Point Format
14 | 7 | Reserved | 402115
15 | 7 | Reserved | 402116
16 | 7 | Reserved | 402117
17 | 7 | Reserved | 402118
18 | 7 | Reserved | 402119
19 | 7 | Reserved | 402120
20 | 7 | Reserved | 402121
21 | 7 | Reserved | 402122
22 | 7 | Reserved | 402123
23 | 7 | Reserved | 402124
24 | 7 | Reserved | 402125
25 | 7 | Reserved | 402126
26 | 7 | Reserved | 402127
27 | 7 | Reserved | 402128
28 | 7 | Reserved | 402129
29 | 7 | Reserved | 402130
30 | 7 | Reserved | 402131
31 | 7 | Reserved | 402132
32 | 7 | Reserved | 402133
33 | 7 | Reserved | 402134
34 | 7 | Reserved | 402135
35 | 7 | Reserved | 402136
36 | 7 | Reserved | 402137
37 | 7 | Reserved | 402138
Meter 8 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Scan Count: process input | 402301
1 | 8 | Scan Count: calculation | 402302
2 | 8 | Meter in Alarm | 402303 | 0=no alarm
3 | 8 | Reserved | 402304
4 | 8 | Net Accumulator | 402305 | Long Integer Format
5 | 8 | Net Accumulator | 402306 | Long Integer Format
6 | 8 | Net Flow Rate | 402307 | Floating Point Format
7 | 8 | Net Flow Rate | 402308 | Floating Point Format
8 | 8 | Gross Flow Rate | 402309 | Floating Point Format
9 | 8 | Gross Flow Rate | 402310 | Floating Point Format
10 | 8 | Fpv | 402311 | Floating Point Format
11 | 8 | Fpv | 402312 | Floating Point Format
12 | 8 | Cprime | 402313 | Floating Point Format
13 | 8 | Cprime | 402314 | Floating Point Format
14 | 8 | Reserved | 402315
15 | 8 | Reserved | 402316
16 | 8 | Reserved | 402317
17 | 8 | Reserved | 402318
18 | 8 | Reserved | 402319
19 | 8 | Reserved | 402320
20 | 8 | Reserved | 402321
21 | 8 | Reserved | 402322
22 | 8 | Reserved | 402323
23 | 8 | Reserved | 402324
24 | 8 | Reserved | 402325
25 | 8 | Reserved | 402326
26 | 8 | Reserved | 402327
27 | 8 | Reserved | 402328
28 | 8 | Reserved | 402329
29 | 8 | Reserved | 402330
30 | 8 | Reserved | 402331
31 | 8 | Reserved | 402332
32 | 8 | Reserved | 402333
33 | 8 | Reserved | 402334
34 | 8 | Reserved | 402335
35 | 8 | Reserved | 402336
36 | 8 | Reserved | 402337
37 | 8 | Reserved | 402338
Meter 9 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Scan Count: process input | 402501
1 | 9 | Scan Count: calculation | 402502
2 | 9 | Meter in Alarm | 402503 | 0=no alarm
3 | 9 | Reserved | 402504
4 | 9 | Net Accumulator | 402505 | Long Integer Format
5 | 9 | Net Accumulator | 402506 | Long Integer Format
6 | 9 | Net Flow Rate | 402507 | Floating Point Format
7 | 9 | Net Flow Rate | 402508 | Floating Point Format
8 | 9 | Gross Flow Rate | 402509 | Floating Point Format
9 | 9 | Gross Flow Rate | 402510 | Floating Point Format
10 | 9 | Fpv | 402511 | Floating Point Format
11 | 9 | Fpv | 402512 | Floating Point Format
12 | 9 | Cprime | 402513 | Floating Point Format
13 | 9 | Cprime | 402514 | Floating Point Format
14 | 9 | Reserved | 402515
15 | 9 | Reserved | 402516
16 | 9 | Reserved | 402517
17 | 9 | Reserved | 402518
18 | 9 | Reserved | 402519
19 | 9 | Reserved | 402520
20 | 9 | Reserved | 402521
21 | 9 | Reserved | 402522
22 | 9 | Reserved | 402523
23 | 9 | Reserved | 402524
24 | 9 | Reserved | 402525
25 | 9 | Reserved | 402526
26 | 9 | Reserved | 402527
27 | 9 | Reserved | 402528
28 | 9 | Reserved | 402529
29 | 9 | Reserved | 402530
30 | 9 | Reserved | 402531
31 | 9 | Reserved | 402532
32 | 9 | Reserved | 402533
33 | 9 | Reserved | 402534
34 | 9 | Reserved | 402535
35 | 9 | Reserved | 402536
36 | 9 | Reserved | 402537
37 | 9 | Reserved | 402538
Meter 10 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Scan Count: process input | 402701
1 | 10 | Scan Count: calculation | 402702
2 | 10 | Meter in Alarm | 402703 | 0=no alarm
3 | 10 | Reserved | 402704
4 | 10 | Net Accumulator | 402705 | Long Integer Format
5 | 10 | Net Accumulator | 402706 | Long Integer Format
6 | 10 | Net Flow Rate | 402707 | Floating Point Format
7 | 10 | Net Flow Rate | 402708 | Floating Point Format
8 | 10 | Gross Flow Rate | 402709 | Floating Point Format
9 | 10 | Gross Flow Rate | 402710 | Floating Point Format
10 | 10 | Fpv | 402711 | Floating Point Format
11 | 10 | Fpv | 402712 | Floating Point Format
12 | 10 | Cprime | 402713 | Floating Point Format
13 | 10 | Cprime | 402714 | Floating Point Format
14 | 10 | Reserved | 402715
15 | 10 | Reserved | 402716
16 | 10 | Reserved | 402717
17 | 10 | Reserved | 402718
18 | 10 | Reserved | 402719
19 | 10 | Reserved | 402720
20 | 10 | Reserved | 402721
21 | 10 | Reserved | 402722
22 | 10 | Reserved | 402723
23 | 10 | Reserved | 402724
24 | 10 | Reserved | 402725
25 | 10 | Reserved | 402726
26 | 10 | Reserved | 402727
27 | 10 | Reserved | 402728
28 | 10 | Reserved | 402729
29 | 10 | Reserved | 402730
30 | 10 | Reserved | 402731
31 | 10 | Reserved | 402732
32 | 10 | Reserved | 402733
33 | 10 | Reserved | 402734
34 | 10 | Reserved | 402735
35 | 10 | Reserved | 402736
36 | 10 | Reserved | 402737
37 | 10 | Reserved | 402738
Meter 11 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Scan Count: process input | 402901
1 | 11 | Scan Count: calculation | 402902
2 | 11 | Meter in Alarm | 402903 | 0=no alarm
3 | 11 | Reserved | 402904
4 | 11 | Net Accumulator | 402905 | Long Integer Format
5 | 11 | Net Accumulator | 402906 | Long Integer Format
6 | 11 | Net Flow Rate | 402907 | Floating Point Format
7 | 11 | Net Flow Rate | 402908 | Floating Point Format
8 | 11 | Gross Flow Rate | 402909 | Floating Point Format
9 | 11 | Gross Flow Rate | 402910 | Floating Point Format
10 | 11 | Fpv | 402911 | Floating Point Format
11 | 11 | Fpv | 402912 | Floating Point Format
12 | 11 | Cprime | 402913 | Floating Point Format
13 | 11 | Cprime | 402914 | Floating Point Format
14 | 11 | Reserved | 402915
15 | 11 | Reserved | 402916
16 | 11 | Reserved | 402917
17 | 11 | Reserved | 402918
18 | 11 | Reserved | 402919
19 | 11 | Reserved | 402920
20 | 11 | Reserved | 402921
21 | 11 | Reserved | 402922
22 | 11 | Reserved | 402923
23 | 11 | Reserved | 402924
24 | 11 | Reserved | 402925
25 | 11 | Reserved | 402926
26 | 11 | Reserved | 402927
27 | 11 | Reserved | 402928
28 | 11 | Reserved | 402929
29 | 11 | Reserved | 402930
30 | 11 | Reserved | 402931
31 | 11 | Reserved | 402932
32 | 11 | Reserved | 402933
33 | 11 | Reserved | 402934
34 | 11 | Reserved | 402935
35 | 11 | Reserved | 402936
36 | 11 | Reserved | 402937
37 | 11 | Reserved | 402938
Meter 12 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Scan Count: process input | 403101
1 | 12 | Scan Count: calculation | 403102
2 | 12 | Meter in Alarm | 403103 | 0=no alarm
3 | 12 | Reserved | 403104
4 | 12 | Net Accumulator | 403105 | Long Integer Format
5 | 12 | Net Accumulator | 403106 | Long Integer Format
6 | 12 | Net Flow Rate | 403107 | Floating Point Format
7 | 12 | Net Flow Rate | 403108 | Floating Point Format
8 | 12 | Gross Flow Rate | 403109 | Floating Point Format
9 | 12 | Gross Flow Rate | 403110 | Floating Point Format
10 | 12 | Fpv | 403111 | Floating Point Format
11 | 12 | Fpv | 403112 | Floating Point Format
12 | 12 | Cprime | 403113 | Floating Point Format
13 | 12 | Cprime | 403114 | Floating Point Format
14 | 12 | Reserved | 403115
15 | 12 | Reserved | 403116
16 | 12 | Reserved | 403117
17 | 12 | Reserved | 403118
18 | 12 | Reserved | 403119
19 | 12 | Reserved | 403120
20 | 12 | Reserved | 403121
21 | 12 | Reserved | 403122
22 | 12 | Reserved | 403123
23 | 12 | Reserved | 403124
24 | 12 | Reserved | 403125
25 | 12 | Reserved | 403126
26 | 12 | Reserved | 403127
27 | 12 | Reserved | 403128
28 | 12 | Reserved | 403129
29 | 12 | Reserved | 403130
30 | 12 | Reserved | 403131
31 | 12 | Reserved | 403132
32 | 12 | Reserved | 403133
33 | 12 | Reserved | 403134
34 | 12 | Reserved | 403135
35 | 12 | Reserved | 403136
36 | 12 | Reserved | 403137
37 | 12 | Reserved | 403138
Meter 13 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Scan Count: process input | 403301
1 | 13 | Scan Count: calculation | 403302
2 | 13 | Meter in Alarm | 403303 | 0=no alarm
3 | 13 | Reserved | 403304
4 | 13 | Net Accumulator | 403305 | Long Integer Format
5 | 13 | Net Accumulator | 403306 | Long Integer Format
6 | 13 | Net Flow Rate | 403307 | Floating Point Format
7 | 13 | Net Flow Rate | 403308 | Floating Point Format
8 | 13 | Gross Flow Rate | 403309 | Floating Point Format
9 | 13 | Gross Flow Rate | 403310 | Floating Point Format
10 | 13 | Fpv | 403311 | Floating Point Format
11 | 13 | Fpv | 403312 | Floating Point Format
12 | 13 | Cprime | 403313 | Floating Point Format
13 | 13 | Cprime | 403314 | Floating Point Format
14 | 13 | Reserved | 403315
15 | 13 | Reserved | 403316
16 | 13 | Reserved | 403317
17 | 13 | Reserved | 403318
18 | 13 | Reserved | 403319
19 | 13 | Reserved | 403320
20 | 13 | Reserved | 403321
21 | 13 | Reserved | 403322
22 | 13 | Reserved | 403323
23 | 13 | Reserved | 403324
24 | 13 | Reserved | 403325
25 | 13 | Reserved | 403326
26 | 13 | Reserved | 403327
27 | 13 | Reserved | 403328
28 | 13 | Reserved | 403329
29 | 13 | Reserved | 403330
30 | 13 | Reserved | 403331
31 | 13 | Reserved | 403332
32 | 13 | Reserved | 403333
33 | 13 | Reserved | 403334
34 | 13 | Reserved | 403335
35 | 13 | Reserved | 403336
36 | 13 | Reserved | 403337
37 | 13 | Reserved | 403338
Meter 14 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Scan Count: process input | 403501
1 | 14 | Scan Count: calculation | 403502
2 | 14 | Meter in Alarm | 403503 | 0=no alarm
3 | 14 | Reserved | 403504
4 | 14 | Net Accumulator | 403505 | Long Integer Format
5 | 14 | Net Accumulator | 403506 | Long Integer Format
6 | 14 | Net Flow Rate | 403507 | Floating Point Format
7 | 14 | Net Flow Rate | 403508 | Floating Point Format
8 | 14 | Gross Flow Rate | 403509 | Floating Point Format
9 | 14 | Gross Flow Rate | 403510 | Floating Point Format
10 | 14 | Fpv | 403511 | Floating Point Format
11 | 14 | Fpv | 403512 | Floating Point Format
12 | 14 | Cprime | 403513 | Floating Point Format
13 | 14 | Cprime | 403514 | Floating Point Format
14 | 14 | Reserved | 403515
15 | 14 | Reserved | 403516
16 | 14 | Reserved | 403517
17 | 14 | Reserved | 403518
18 | 14 | Reserved | 403519
19 | 14 | Reserved | 403520
20 | 14 | Reserved | 403521
21 | 14 | Reserved | 403522
22 | 14 | Reserved | 403523
23 | 14 | Reserved | 403524
24 | 14 | Reserved | 403525
25 | 14 | Reserved | 403526
26 | 14 | Reserved | 403527
27 | 14 | Reserved | 403528
28 | 14 | Reserved | 403529
29 | 14 | Reserved | 403530
30 | 14 | Reserved | 403531
31 | 14 | Reserved | 403532
32 | 14 | Reserved | 403533
33 | 14 | Reserved | 403534
34 | 14 | Reserved | 403535
35 | 14 | Reserved | 403536
36 | 14 | Reserved | 403537
37 | 14 | Reserved | 403538
Meter 15 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Scan Count: process input | 403701
1 | 15 | Scan Count: calculation | 403702
2 | 15 | Meter in Alarm | 403703 | 0=no alarm
3 | 15 | Reserved | 403704
4 | 15 | Net Accumulator | 403705 | Long Integer Format
5 | 15 | Net Accumulator | 403706 | Long Integer Format
6 | 15 | Net Flow Rate | 403707 | Floating Point Format
7 | 15 | Net Flow Rate | 403708 | Floating Point Format
8 | 15 | Gross Flow Rate | 403709 | Floating Point Format
9 | 15 | Gross Flow Rate | 403710 | Floating Point Format
10 | 15 | Fpv | 403711 | Floating Point Format
11 | 15 | Fpv | 403712 | Floating Point Format
12 | 15 | Cprime | 403713 | Floating Point Format
13 | 15 | Cprime | 403714 | Floating Point Format
14 | 15 | Reserved | 403715
15 | 15 | Reserved | 403716
16 | 15 | Reserved | 403717
17 | 15 | Reserved | 403718
18 | 15 | Reserved | 403719
19 | 15 | Reserved | 403720
20 | 15 | Reserved | 403721
21 | 15 | Reserved | 403722
22 | 15 | Reserved | 403723
23 | 15 | Reserved | 403724
24 | 15 | Reserved | 403725
25 | 15 | Reserved | 403726
26 | 15 | Reserved | 403727
27 | 15 | Reserved | 403728
28 | 15 | Reserved | 403729
29 | 15 | Reserved | 403730
30 | 15 | Reserved | 403731
31 | 15 | Reserved | 403732
32 | 15 | Reserved | 403733
33 | 15 | Reserved | 403734
34 | 15 | Reserved | 403735
35 | 15 | Reserved | 403736
36 | 15 | Reserved | 403737
37 | 15 | Reserved | 403738
Meter 16 Results Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Scan Count: process input | 403901
1 | 16 | Scan Count: calculation | 403902
2 | 16 | Meter in Alarm | 403903 | 0=no alarm
3 | 16 | Reserved | 403904
4 | 16 | Net Accumulator | 403905 | Long Integer Format
5 | 16 | Net Accumulator | 403906 | Long Integer Format
6 | 16 | Net Flow Rate | 403907 | Floating Point Format
7 | 16 | Net Flow Rate | 403908 | Floating Point Format
8 | 16 | Gross Flow Rate | 403909 | Floating Point Format
9 | 16 | Gross Flow Rate | 403910 | Floating Point Format
10 | 16 | Fpv | 403911 | Floating Point Format
11 | 16 | Fpv | 403912 | Floating Point Format
12 | 16 | Cprime | 403913 | Floating Point Format
13 | 16 | Cprime | 403914 | Floating Point Format
14 | 16 | Reserved | 403915
15 | 16 | Reserved | 403916
16 | 16 | Reserved | 403917
17 | 16 | Reserved | 403918
18 | 16 | Reserved | 403919
19 | 16 | Reserved | 403920
20 | 16 | Reserved | 403921
21 | 16 | Reserved | 403922
22 | 16 | Reserved | 403923
23 | 16 | Reserved | 403924
24 | 16 | Reserved | 403925
25 | 16 | Reserved | 403926
26 | 16 | Reserved | 403927
27 | 16 | Reserved | 403928
28 | 16 | Reserved | 403929
29 | 16 | Reserved | 403930
30 | 16 | Reserved | 403931
31 | 16 | Reserved | 403932
32 | 16 | Reserved | 403933
33 | 16 | Reserved | 403934
34 | 16 | Reserved | 403935
35 | 16 | Reserved | 403936
36 | 16 | Reserved | 403937
37 | 16 | Reserved | 403938

## Meter Variables - Orifice & Liq
Meter 1 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Meter Disable | 400801
1 | 1 | Water% | 400802 | Scaled Integer Format
2 | 1 | Temperature | 400803 | Floating Point Format
3 | 1 | Temperature | 400804 | Floating Point Format
4 | 1 | Pressure | 400805 | Floating Point Format
5 | 1 | Pressure | 400806 | Floating Point Format
6 | 1 | Differential Pressure | 400807 | Floating Point Format
7 | 1 | Differential Pressure | 400808 | Floating Point Format
8 | 1 | Density | 400809 | Floating Point Format
9 | 1 | Density | 400810 | Floating Point Format
10 | 1 | Reserved | 400811
11 | 1 | Reserved | 400812
12 | 1 | Molar Analysis - C1 | 400813 | Scaled Integer Format (10000 = 100%)
13 | 1 | Molar Analysis - N2 | 400814 | Scaled Integer Format (10000 = 100%)
14 | 1 | Molar Analysis - CO2 | 400815 | Scaled Integer Format (10000 = 100%)
15 | 1 | Molar Analysis - C2 | 400816 | Scaled Integer Format (10000 = 100%)
16 | 1 | Molar Analysis - C3 | 400817 | Scaled Integer Format (10000 = 100%)
17 | 1 | Molar Analysis - H2O | 400818 | Scaled Integer Format (10000 = 100%)
18 | 1 | Molar Analysis - H2S | 400819 | Scaled Integer Format (10000 = 100%)
19 | 1 | Molar Analysis - H2 | 400820 | Scaled Integer Format (10000 = 100%)
20 | 1 | Molar Analysis - CO | 400821 | Scaled Integer Format (10000 = 100%)
21 | 1 | Molar Analysis - O2 | 400822 | Scaled Integer Format (10000 = 100%)
22 | 1 | Molar Analysis - iC4 | 400823 | Scaled Integer Format (10000 = 100%)
23 | 1 | Molar Analysis - C4 | 400824 | Scaled Integer Format (10000 = 100%)
24 | 1 | Molar Analysis - iC5 | 400825 | Scaled Integer Format (10000 = 100%)
25 | 1 | Molar Analysis - C5 | 400826 | Scaled Integer Format (10000 = 100%)
26 | 1 | Molar Analysis - C6 | 400827 | Scaled Integer Format (10000 = 100%)
27 | 1 | Molar Analysis - C7 | 400828 | Scaled Integer Format (10000 = 100%)
28 | 1 | Molar Analysis - C8 | 400829 | Scaled Integer Format (10000 = 100%)
29 | 1 | Molar Analysis - C9 | 400830 | Scaled Integer Format (10000 = 100%)
30 | 1 | Molar Analysis - C10 | 400831 | Scaled Integer Format (10000 = 100%)
31 | 1 | Molar Analysis - He | 400832 | Scaled Integer Format (10000 = 100%)
32 | 1 | Molar Analysis - Ar | 400833 | Scaled Integer Format (10000 = 100%)
33 | 1 | Molar Analysis - C5 (neo-p) | 400834 | Scaled Integer Format (10000 = 100%)
34 | 1 | Molar Analysis - Ux | 400835 | Scaled Integer Format (10000 = 100%)
35 | 1 | Molar Analysis - Uy | 400836 | Scaled Integer Format (10000 = 100%)
36 | 1 | Meter Signals - Reserved | 400837
37 | 1 | Meter Signals - Reserved | 400838
38 | 1 | Meter Signals - Reserved | 400839
39 | 1 | Meter Signals - Reserved | 400840
40 | 1 | Meter Signals - Reset Acc 1 | 400841
41 | 1 | Meter Signals - Reset Acc 2 | 400842
42 | 1 | Meter Signals - Reset Acc 3 | 400843
43 | 1 | Meter Signals - Reset Acc 4 | 400844
44 | 1 | Write Daily Archive | 400845
45 | 1 | Write Hourly Archive | 400846
46 | 1 | Meter Signals - Reserved | 400847
47 | 1 | Meter Signals - Reserved | 400848
48 | 1 | Meter Signals - Reserved | 400849
49 | 1 | Meter Signals - Reserved | 400850
50 | 1 | Meter Signals - Reserved | 400851
51 | 1 | Meter Signals - Reserved | 400852
52 | 1 | Analysis is Present | 400853
53 | 1 | Meter Archive Record Fetch | 400854 | (=0 signal not present)
54 | 1 | Meter Archive Record Age | 400855 | (=0 current)
55 | 1 | Meter Archive File Select | 400856 | (=0 daily, 1=hourly)
Meter 2 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Meter Disable | 401001
1 | 2 | Water % | 401002 | Scaled Integer Format
2 | 2 | Temperature | 401003 | Floating Point Format
3 | 2 | Temperature | 401004 | Floating Point Format
4 | 2 | Pressure | 401005 | Floating Point Format
5 | 2 | Pressure | 401006 | Floating Point Format
6 | 2 | Differential Pressure | 401007 | Floating Point Format
7 | 2 | Differential Pressure | 401008 | Floating Point Format
8 | 2 | Density | 401009 | Floating Point Format
9 | 2 | Density | 401010 | Floating Point Format
10 | 2 | Reserved | 401011
11 | 2 | Reserved | 401012
12 | 2 | Molar Analysis - C1 | 401013 | Scaled Integer Format (10000 = 100%)
13 | 2 | Molar Analysis - N2 | 401014 | Scaled Integer Format (10000 = 100%)
14 | 2 | Molar Analysis - CO2 | 401015 | Scaled Integer Format (10000 = 100%)
15 | 2 | Molar Analysis - C2 | 401016 | Scaled Integer Format (10000 = 100%)
16 | 2 | Molar Analysis - C3 | 401017 | Scaled Integer Format (10000 = 100%)
17 | 2 | Molar Analysis - H2O | 401018 | Scaled Integer Format (10000 = 100%)
18 | 2 | Molar Analysis - H2S | 401019 | Scaled Integer Format (10000 = 100%)
19 | 2 | Molar Analysis - H2 | 401020 | Scaled Integer Format (10000 = 100%)
20 | 2 | Molar Analysis - CO | 401021 | Scaled Integer Format (10000 = 100%)
21 | 2 | Molar Analysis - O2 | 401022 | Scaled Integer Format (10000 = 100%)
22 | 2 | Molar Analysis - iC4 | 401023 | Scaled Integer Format (10000 = 100%)
23 | 2 | Molar Analysis - C4 | 401024 | Scaled Integer Format (10000 = 100%)
24 | 2 | Molar Analysis - iC5 | 401025 | Scaled Integer Format (10000 = 100%)
25 | 2 | Molar Analysis - C5 | 401026 | Scaled Integer Format (10000 = 100%)
26 | 2 | Molar Analysis - C6 | 401027 | Scaled Integer Format (10000 = 100%)
27 | 2 | Molar Analysis - C7 | 401028 | Scaled Integer Format (10000 = 100%)
28 | 2 | Molar Analysis - C8 | 401029 | Scaled Integer Format (10000 = 100%)
29 | 2 | Molar Analysis - C9 | 401030 | Scaled Integer Format (10000 = 100%)
30 | 2 | Molar Analysis - C10 | 401031 | Scaled Integer Format (10000 = 100%)
31 | 2 | Molar Analysis - He | 401032 | Scaled Integer Format (10000 = 100%)
32 | 2 | Molar Analysis - Ar | 401033 | Scaled Integer Format (10000 = 100%)
33 | 2 | Molar Analysis - C5 (neo-p) | 401034 | Scaled Integer Format (10000 = 100%)
34 | 2 | Molar Analysis - Ux | 401035 | Scaled Integer Format (10000 = 100%)
35 | 2 | Molar Analysis - Uy | 401036 | Scaled Integer Format (10000 = 100%)
36 | 2 | Meter Signals - Reserved | 401037
37 | 2 | Meter Signals - Reserved | 401038
38 | 2 | Meter Signals - Reserved | 401039
39 | 2 | Meter Signals - Reserved | 401040
40 | 2 | Meter Signals - Reset Acc 1 | 401041
41 | 2 | Meter Signals - Reset Acc 2 | 401042
42 | 2 | Meter Signals - Reset Acc 3 | 401043
43 | 2 | Meter Signals - Reset Acc 4 | 401044
44 | 2 | Write Daily Archive | 401045
45 | 2 | Write Hourly Archive | 401046
46 | 2 | Meter Signals - Reserved | 401047
47 | 2 | Meter Signals - Reserved | 401048
48 | 2 | Meter Signals - Reserved | 401049
49 | 2 | Meter Signals - Reserved | 401050
50 | 2 | Meter Signals - Reserved | 401051
51 | 2 | Meter Signals - Reserved | 401052
52 | 2 | Analysis is Present | 401053
53 | 2 | Meter Archive Record Fetch | 401054 | (=0 signal not present)
54 | 2 | Meter Archive Record Age | 401055 | (=0 current)
55 | 2 | Meter Archive File Select | 401056 | (=0 daily, 1=hourly)
Meter 3 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Meter Disable | 401201
1 | 3 | Water % | 401202 | Scaled Integer Format
2 | 3 | Temperature | 401203 | Floating Point Format
3 | 3 | Temperature | 401204 | Floating Point Format
4 | 3 | Pressure | 401205 | Floating Point Format
5 | 3 | Pressure | 401206 | Floating Point Format
6 | 3 | Differential Pressure | 401207 | Floating Point Format
7 | 3 | Differential Pressure | 401208 | Floating Point Format
8 | 3 | Density | 401209 | Floating Point Format
9 | 3 | Density | 401210 | Floating Point Format
10 | 3 | Reserved | 401211
11 | 3 | Reserved | 401212
12 | 3 | Molar Analysis - C1 | 401213 | Scaled Integer Format (10000 = 100%)
13 | 3 | Molar Analysis - N2 | 401214 | Scaled Integer Format (10000 = 100%)
14 | 3 | Molar Analysis - CO2 | 401215 | Scaled Integer Format (10000 = 100%)
15 | 3 | Molar Analysis - C2 | 401216 | Scaled Integer Format (10000 = 100%)
16 | 3 | Molar Analysis - C3 | 401217 | Scaled Integer Format (10000 = 100%)
17 | 3 | Molar Analysis - H2O | 401218 | Scaled Integer Format (10000 = 100%)
18 | 3 | Molar Analysis - H2S | 401219 | Scaled Integer Format (10000 = 100%)
19 | 3 | Molar Analysis - H2 | 401220 | Scaled Integer Format (10000 = 100%)
20 | 3 | Molar Analysis - CO | 401221 | Scaled Integer Format (10000 = 100%)
21 | 3 | Molar Analysis - O2 | 401222 | Scaled Integer Format (10000 = 100%)
22 | 3 | Molar Analysis - iC4 | 401223 | Scaled Integer Format (10000 = 100%)
23 | 3 | Molar Analysis - C4 | 401224 | Scaled Integer Format (10000 = 100%)
24 | 3 | Molar Analysis - iC5 | 401225 | Scaled Integer Format (10000 = 100%)
25 | 3 | Molar Analysis - C5 | 401226 | Scaled Integer Format (10000 = 100%)
26 | 3 | Molar Analysis - C6 | 401227 | Scaled Integer Format (10000 = 100%)
27 | 3 | Molar Analysis - C7 | 401228 | Scaled Integer Format (10000 = 100%)
28 | 3 | Molar Analysis - C8 | 401229 | Scaled Integer Format (10000 = 100%)
29 | 3 | Molar Analysis - C9 | 401230 | Scaled Integer Format (10000 = 100%)
30 | 3 | Molar Analysis - C10 | 401231 | Scaled Integer Format (10000 = 100%)
31 | 3 | Molar Analysis - He | 401232 | Scaled Integer Format (10000 = 100%)
32 | 3 | Molar Analysis - Ar | 401233 | Scaled Integer Format (10000 = 100%)
33 | 3 | Molar Analysis - C5 (neo-p) | 401234 | Scaled Integer Format (10000 = 100%)
34 | 3 | Molar Analysis - Ux | 401235 | Scaled Integer Format (10000 = 100%)
35 | 3 | Molar Analysis - Uy | 401236 | Scaled Integer Format (10000 = 100%)
36 | 3 | Meter Signals - Reserved | 401237
37 | 3 | Meter Signals - Reserved | 401238
38 | 3 | Meter Signals - Reserved | 401239
39 | 3 | Meter Signals - Reserved | 401240
40 | 3 | Meter Signals - Reset Acc 1 | 401241
41 | 3 | Meter Signals - Reset Acc 2 | 401242
42 | 3 | Meter Signals - Reset Acc 3 | 401243
43 | 3 | Meter Signals - Reset Acc 4 | 401244
44 | 3 | Write Daily Archive | 401245
45 | 3 | Write Hourly Archive | 401246
46 | 3 | Meter Signals - Reserved | 401247
47 | 3 | Meter Signals - Reserved | 401248
48 | 3 | Meter Signals - Reserved | 401249
49 | 3 | Meter Signals - Reserved | 401250
50 | 3 | Meter Signals - Reserved | 401251
51 | 3 | Meter Signals - Reserved | 401252
52 | 3 | Analysis is Present | 401253
53 | 3 | Meter Archive Record Fetch | 401254 | (=0 signal not present)
54 | 3 | Meter Archive Record Age | 401255 | (=0 current)
55 | 3 | Meter Archive File Select | 401256 | (=0 daily, 1=hourly)
Meter 4 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Meter Disable | 401401
1 | 4 | Water% | 401402 | Scaled Integer Format
2 | 4 | Temperature | 401403 | Floating Point Format
3 | 4 | Temperature | 401404 | Floating Point Format
4 | 4 | Pressure | 401405 | Floating Point Format
5 | 4 | Pressure | 401406 | Floating Point Format
6 | 4 | Differential Pressure | 401407 | Floating Point Format
7 | 4 | Differential Pressure | 401408 | Floating Point Format
8 | 4 | Density | 401409 | Floating Point Format
9 | 4 | Density | 401410 | Floating Point Format
10 | 4 | Reserved | 401411
11 | 4 | Reserved | 401412
12 | 4 | Molar Analysis - C1 | 401413 | Scaled Integer Format (10000 = 100%)
13 | 4 | Molar Analysis - N2 | 401414 | Scaled Integer Format (10000 = 100%)
14 | 4 | Molar Analysis - CO2 | 401415 | Scaled Integer Format (10000 = 100%)
15 | 4 | Molar Analysis - C2 | 401416 | Scaled Integer Format (10000 = 100%)
16 | 4 | Molar Analysis - C3 | 401417 | Scaled Integer Format (10000 = 100%)
17 | 4 | Molar Analysis - H2O | 401418 | Scaled Integer Format (10000 = 100%)
18 | 4 | Molar Analysis - H2S | 401419 | Scaled Integer Format (10000 = 100%)
19 | 4 | Molar Analysis - H2 | 401420 | Scaled Integer Format (10000 = 100%)
20 | 4 | Molar Analysis - CO | 401421 | Scaled Integer Format (10000 = 100%)
21 | 4 | Molar Analysis - O2 | 401422 | Scaled Integer Format (10000 = 100%)
22 | 4 | Molar Analysis - iC4 | 401423 | Scaled Integer Format (10000 = 100%)
23 | 4 | Molar Analysis - C4 | 401424 | Scaled Integer Format (10000 = 100%)
24 | 4 | Molar Analysis - iC5 | 401425 | Scaled Integer Format (10000 = 100%)
25 | 4 | Molar Analysis - C5 | 401426 | Scaled Integer Format (10000 = 100%)
26 | 4 | Molar Analysis - C6 | 401427 | Scaled Integer Format (10000 = 100%)
27 | 4 | Molar Analysis - C7 | 401428 | Scaled Integer Format (10000 = 100%)
28 | 4 | Molar Analysis - C8 | 401429 | Scaled Integer Format (10000 = 100%)
29 | 4 | Molar Analysis - C9 | 401430 | Scaled Integer Format (10000 = 100%)
30 | 4 | Molar Analysis - C10 | 401431 | Scaled Integer Format (10000 = 100%)
31 | 4 | Molar Analysis - He | 401432 | Scaled Integer Format (10000 = 100%)
32 | 4 | Molar Analysis - Ar | 401433 | Scaled Integer Format (10000 = 100%)
33 | 4 | Molar Analysis - C5 (neo-p) | 401434 | Scaled Integer Format (10000 = 100%)
34 | 4 | Molar Analysis - Ux | 401435 | Scaled Integer Format (10000 = 100%)
35 | 4 | Molar Analysis - Uy | 401436 | Scaled Integer Format (10000 = 100%)
36 | 4 | Meter Signals - Reserved | 401437
37 | 4 | Meter Signals - Reserved | 401438
38 | 4 | Meter Signals - Reserved | 401439
39 | 4 | Meter Signals - Reserved | 401440
40 | 4 | Meter Signals - Reset Acc 1 | 401441
41 | 4 | Meter Signals - Reset Acc 2 | 401442
42 | 4 | Meter Signals - Reset Acc 3 | 401443
43 | 4 | Meter Signals - Reset Acc 4 | 401444
44 | 4 | Write Daily Archive | 401445
45 | 4 | Write Hourly Archive | 401446
46 | 4 | Meter Signals - Reserved | 401447
47 | 4 | Meter Signals - Reserved | 401448
48 | 4 | Meter Signals - Reserved | 401449
49 | 4 | Meter Signals - Reserved | 401450
50 | 4 | Meter Signals - Reserved | 401451
51 | 4 | Meter Signals - Reserved | 401452
52 | 4 | Analysis is Present | 401453
53 | 4 | Meter Archive Record Fetch | 401454 | (=0 signal not present)
54 | 4 | Meter Archive Record Age | 401455 | (=0 current)
55 | 4 | Meter Archive File Select | 401456 | (=0 daily, 1=hourly)
Meter 5 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Meter Disable | 401601
1 | 5 | Water % | 401602 | Scaled Integer Format
2 | 5 | Temperature | 401603 | Floating Point Format
3 | 5 | Temperature | 401604 | Floating Point Format
4 | 5 | Pressure | 401605 | Floating Point Format
5 | 5 | Pressure | 401606 | Floating Point Format
6 | 5 | Differential Pressure | 401607 | Floating Point Format
7 | 5 | Differential Pressure | 401608 | Floating Point Format
8 | 5 | Density | 401609 | Floating Point Format
9 | 5 | Density | 401610 | Floating Point Format
10 | 5 | Reserved | 401611
11 | 5 | Reserved | 401612
12 | 5 | Molar Analysis - C1 | 401613 | Scaled Integer Format (10000 = 100%)
13 | 5 | Molar Analysis - N2 | 401614 | Scaled Integer Format (10000 = 100%)
14 | 5 | Molar Analysis - CO2 | 401615 | Scaled Integer Format (10000 = 100%)
15 | 5 | Molar Analysis - C2 | 401616 | Scaled Integer Format (10000 = 100%)
16 | 5 | Molar Analysis - C3 | 401617 | Scaled Integer Format (10000 = 100%)
17 | 5 | Molar Analysis - H2O | 401618 | Scaled Integer Format (10000 = 100%)
18 | 5 | Molar Analysis - H2S | 401619 | Scaled Integer Format (10000 = 100%)
19 | 5 | Molar Analysis - H2 | 401620 | Scaled Integer Format (10000 = 100%)
20 | 5 | Molar Analysis - CO | 401621 | Scaled Integer Format (10000 = 100%)
21 | 5 | Molar Analysis - O2 | 401622 | Scaled Integer Format (10000 = 100%)
22 | 5 | Molar Analysis - iC4 | 401623 | Scaled Integer Format (10000 = 100%)
23 | 5 | Molar Analysis - C4 | 401624 | Scaled Integer Format (10000 = 100%)
24 | 5 | Molar Analysis - iC5 | 401625 | Scaled Integer Format (10000 = 100%)
25 | 5 | Molar Analysis - C5 | 401626 | Scaled Integer Format (10000 = 100%)
26 | 5 | Molar Analysis - C6 | 401627 | Scaled Integer Format (10000 = 100%)
27 | 5 | Molar Analysis - C7 | 401628 | Scaled Integer Format (10000 = 100%)
28 | 5 | Molar Analysis - C8 | 401629 | Scaled Integer Format (10000 = 100%)
29 | 5 | Molar Analysis - C9 | 401630 | Scaled Integer Format (10000 = 100%)
30 | 5 | Molar Analysis - C10 | 401631 | Scaled Integer Format (10000 = 100%)
31 | 5 | Molar Analysis - He | 401632 | Scaled Integer Format (10000 = 100%)
32 | 5 | Molar Analysis - Ar | 401633 | Scaled Integer Format (10000 = 100%)
33 | 5 | Molar Analysis - C5 (neo-p) | 401634 | Scaled Integer Format (10000 = 100%)
34 | 5 | Molar Analysis - Ux | 401635 | Scaled Integer Format (10000 = 100%)
35 | 5 | Molar Analysis - Uy | 401636 | Scaled Integer Format (10000 = 100%)
36 | 5 | Meter Signals - Reserved | 401637
37 | 5 | Meter Signals - Reserved | 401638
38 | 5 | Meter Signals - Reserved | 401639
39 | 5 | Meter Signals - Reserved | 401640
40 | 5 | Meter Signals - Reset Acc 1 | 401641
41 | 5 | Meter Signals - Reset Acc 2 | 401642
42 | 5 | Meter Signals - Reset Acc 3 | 401643
43 | 5 | Meter Signals - Reset Acc 4 | 401644
44 | 5 | Write Daily Archive | 401645
45 | 5 | Write Hourly Archive | 401646
46 | 5 | Meter Signals - Reserved | 401647
47 | 5 | Meter Signals - Reserved | 401648
48 | 5 | Meter Signals - Reserved | 401649
49 | 5 | Meter Signals - Reserved | 401650
50 | 5 | Meter Signals - Reserved | 401651
51 | 5 | Meter Signals - Reserved | 401652
52 | 5 | Analysis is Present | 401653
53 | 5 | Meter Archive Record Fetch | 401654 | (=0 signal not present)
54 | 5 | Meter Archive Record Age | 401655 | (=0 current)
55 | 5 | Meter Archive File Select | 401656 | (=0 daily, 1=hourly)
Meter 6 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Meter Disable | 401801
1 | 6 | Water % | 401802 | Scaled Integer Format
2 | 6 | Temperature | 401803 | Floating Point Format
3 | 6 | Temperature | 401804 | Floating Point Format
4 | 6 | Pressure | 401805 | Floating Point Format
5 | 6 | Pressure | 401806 | Floating Point Format
6 | 6 | Differential Pressure | 401807 | Floating Point Format
7 | 6 | Differential Pressure | 401808 | Floating Point Format
8 | 6 | Density | 401809 | Floating Point Format
9 | 6 | Density | 401810 | Floating Point Format
10 | 6 | Reserved | 401811
11 | 6 | Reserved | 401812
12 | 6 | Molar Analysis - C1 | 401813 | Scaled Integer Format (10000 = 100%)
13 | 6 | Molar Analysis - N2 | 401814 | Scaled Integer Format (10000 = 100%)
14 | 6 | Molar Analysis - CO2 | 401815 | Scaled Integer Format (10000 = 100%)
15 | 6 | Molar Analysis - C2 | 401816 | Scaled Integer Format (10000 = 100%)
16 | 6 | Molar Analysis - C3 | 401817 | Scaled Integer Format (10000 = 100%)
17 | 6 | Molar Analysis - H2O | 401818 | Scaled Integer Format (10000 = 100%)
18 | 6 | Molar Analysis - H2S | 401819 | Scaled Integer Format (10000 = 100%)
19 | 6 | Molar Analysis - H2 | 401820 | Scaled Integer Format (10000 = 100%)
20 | 6 | Molar Analysis - CO | 401821 | Scaled Integer Format (10000 = 100%)
21 | 6 | Molar Analysis - O2 | 401822 | Scaled Integer Format (10000 = 100%)
22 | 6 | Molar Analysis - iC4 | 401823 | Scaled Integer Format (10000 = 100%)
23 | 6 | Molar Analysis - C4 | 401824 | Scaled Integer Format (10000 = 100%)
24 | 6 | Molar Analysis - iC5 | 401825 | Scaled Integer Format (10000 = 100%)
25 | 6 | Molar Analysis - C5 | 401826 | Scaled Integer Format (10000 = 100%)
26 | 6 | Molar Analysis - C6 | 401827 | Scaled Integer Format (10000 = 100%)
27 | 6 | Molar Analysis - C7 | 401828 | Scaled Integer Format (10000 = 100%)
28 | 6 | Molar Analysis - C8 | 401829 | Scaled Integer Format (10000 = 100%)
29 | 6 | Molar Analysis - C9 | 401830 | Scaled Integer Format (10000 = 100%)
30 | 6 | Molar Analysis - C10 | 401831 | Scaled Integer Format (10000 = 100%)
31 | 6 | Molar Analysis - He | 401832 | Scaled Integer Format (10000 = 100%)
32 | 6 | Molar Analysis - Ar | 401833 | Scaled Integer Format (10000 = 100%)
33 | 6 | Molar Analysis - C5 (neo-p) | 401834 | Scaled Integer Format (10000 = 100%)
34 | 6 | Molar Analysis - Ux | 401835 | Scaled Integer Format (10000 = 100%)
35 | 6 | Molar Analysis - Uy | 401836 | Scaled Integer Format (10000 = 100%)
36 | 6 | Meter Signals - Reserved | 401837
37 | 6 | Meter Signals - Reserved | 401838
38 | 6 | Meter Signals - Reserved | 401839
39 | 6 | Meter Signals - Reserved | 401840
40 | 6 | Meter Signals - Reset Acc 1 | 401841
41 | 6 | Meter Signals - Reset Acc 2 | 401842
42 | 6 | Meter Signals - Reset Acc 3 | 401843
43 | 6 | Meter Signals - Reset Acc 4 | 401844
44 | 6 | Write Daily Archive | 401845
45 | 6 | Write Hourly Archive | 401846
46 | 6 | Meter Signals - Reserved | 401847
47 | 6 | Meter Signals - Reserved | 401848
48 | 6 | Meter Signals - Reserved | 401849
49 | 6 | Meter Signals - Reserved | 401850
50 | 6 | Meter Signals - Reserved | 401851
51 | 6 | Meter Signals - Reserved | 401852
52 | 6 | Analysis is Present | 401853
53 | 6 | Meter Archive Record Fetch | 401854 | (=0 signal not present)
54 | 6 | Meter Archive Record Age | 401855 | (=0 current)
55 | 6 | Meter Archive File Select | 401856 | (=0 daily, 1=hourly)
Meter 7 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Meter Disable | 402001
1 | 7 | Water % | 402002 | Scaled Integer Format
2 | 7 | Temperature | 402003 | Floating Point Format
3 | 7 | Temperature | 402004 | Floating Point Format
4 | 7 | Pressure | 402005 | Floating Point Format
5 | 7 | Pressure | 402006 | Floating Point Format
6 | 7 | Differential Pressure | 402007 | Floating Point Format
7 | 7 | Differential Pressure | 402008 | Floating Point Format
8 | 7 | Density | 402009 | Floating Point Format
9 | 7 | Density | 402010 | Floating Point Format
10 | 7 | Reserved | 402011
11 | 7 | Reserved | 402012
12 | 7 | Molar Analysis - C1 | 402013 | Scaled Integer Format (10000 = 100%)
13 | 7 | Molar Analysis - N2 | 402014 | Scaled Integer Format (10000 = 100%)
14 | 7 | Molar Analysis - CO2 | 402015 | Scaled Integer Format (10000 = 100%)
15 | 7 | Molar Analysis - C2 | 402016 | Scaled Integer Format (10000 = 100%)
16 | 7 | Molar Analysis - C3 | 402017 | Scaled Integer Format (10000 = 100%)
17 | 7 | Molar Analysis - H2O | 402018 | Scaled Integer Format (10000 = 100%)
18 | 7 | Molar Analysis - H2S | 402019 | Scaled Integer Format (10000 = 100%)
19 | 7 | Molar Analysis - H2 | 402020 | Scaled Integer Format (10000 = 100%)
20 | 7 | Molar Analysis - CO | 402021 | Scaled Integer Format (10000 = 100%)
21 | 7 | Molar Analysis - O2 | 402022 | Scaled Integer Format (10000 = 100%)
22 | 7 | Molar Analysis - iC4 | 402023 | Scaled Integer Format (10000 = 100%)
23 | 7 | Molar Analysis - C4 | 402024 | Scaled Integer Format (10000 = 100%)
24 | 7 | Molar Analysis - iC5 | 402025 | Scaled Integer Format (10000 = 100%)
25 | 7 | Molar Analysis - C5 | 402026 | Scaled Integer Format (10000 = 100%)
26 | 7 | Molar Analysis - C6 | 402027 | Scaled Integer Format (10000 = 100%)
27 | 7 | Molar Analysis - C7 | 402028 | Scaled Integer Format (10000 = 100%)
28 | 7 | Molar Analysis - C8 | 402029 | Scaled Integer Format (10000 = 100%)
29 | 7 | Molar Analysis - C9 | 402030 | Scaled Integer Format (10000 = 100%)
30 | 7 | Molar Analysis - C10 | 402031 | Scaled Integer Format (10000 = 100%)
31 | 7 | Molar Analysis - He | 402032 | Scaled Integer Format (10000 = 100%)
32 | 7 | Molar Analysis - Ar | 402033 | Scaled Integer Format (10000 = 100%)
33 | 7 | Molar Analysis - C5 (neo-p) | 402034 | Scaled Integer Format (10000 = 100%)
34 | 7 | Molar Analysis - Ux | 402035 | Scaled Integer Format (10000 = 100%)
35 | 7 | Molar Analysis - Uy | 402036 | Scaled Integer Format (10000 = 100%)
36 | 7 | Meter Signals - Reserved | 402037
37 | 7 | Meter Signals - Reserved | 402038
38 | 7 | Meter Signals - Reserved | 402039
39 | 7 | Meter Signals - Reserved | 402040
40 | 7 | Meter Signals - Reset Acc 1 | 402041
41 | 7 | Meter Signals - Reset Acc 2 | 402042
42 | 7 | Meter Signals - Reset Acc 3 | 402043
43 | 7 | Meter Signals - Reset Acc 4 | 402044
44 | 7 | Write Daily Archive | 402045
45 | 7 | Write Hourly Archive | 402046
46 | 7 | Meter Signals - Reserved | 402047
47 | 7 | Meter Signals - Reserved | 402048
48 | 7 | Meter Signals - Reserved | 402049
49 | 7 | Meter Signals - Reserved | 402050
50 | 7 | Meter Signals - Reserved | 402051
51 | 7 | Meter Signals - Reserved | 402052
52 | 7 | Analysis is Present | 402053
53 | 7 | Meter Archive Record Fetch | 402054 | (=0 signal not present)
54 | 7 | Meter Archive Record Age | 402055 | (=0 current)
55 | 7 | Meter Archive File Select | 402056 | (=0 daily, 1=hourly)
Meter 8 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Meter Disable | 402201
1 | 8 | Water % | 402202 | Scaled Integer Format
2 | 8 | Temperature | 402203 | Floating Point Format
3 | 8 | Temperature | 402204 | Floating Point Format
4 | 8 | Pressure | 402205 | Floating Point Format
5 | 8 | Pressure | 402206 | Floating Point Format
6 | 8 | Differential Pressure | 402207 | Floating Point Format
7 | 8 | Differential Pressure | 402208 | Floating Point Format
8 | 8 | Density | 402209 | Floating Point Format
9 | 8 | Density | 402210 | Floating Point Format
10 | 8 | Reserved | 402211
11 | 8 | Reserved | 402212
12 | 8 | Molar Analysis - C1 | 402213 | Scaled Integer Format (10000 = 100%)
13 | 8 | Molar Analysis - N2 | 402214 | Scaled Integer Format (10000 = 100%)
14 | 8 | Molar Analysis - CO2 | 402215 | Scaled Integer Format (10000 = 100%)
15 | 8 | Molar Analysis - C2 | 402216 | Scaled Integer Format (10000 = 100%)
16 | 8 | Molar Analysis - C3 | 402217 | Scaled Integer Format (10000 = 100%)
17 | 8 | Molar Analysis - H2O | 402218 | Scaled Integer Format (10000 = 100%)
18 | 8 | Molar Analysis - H2S | 402219 | Scaled Integer Format (10000 = 100%)
19 | 8 | Molar Analysis - H2 | 402220 | Scaled Integer Format (10000 = 100%)
20 | 8 | Molar Analysis - CO | 402221 | Scaled Integer Format (10000 = 100%)
21 | 8 | Molar Analysis - O2 | 402222 | Scaled Integer Format (10000 = 100%)
22 | 8 | Molar Analysis - iC4 | 402223 | Scaled Integer Format (10000 = 100%)
23 | 8 | Molar Analysis - C4 | 402224 | Scaled Integer Format (10000 = 100%)
24 | 8 | Molar Analysis - iC5 | 402225 | Scaled Integer Format (10000 = 100%)
25 | 8 | Molar Analysis - C5 | 402226 | Scaled Integer Format (10000 = 100%)
26 | 8 | Molar Analysis - C6 | 402227 | Scaled Integer Format (10000 = 100%)
27 | 8 | Molar Analysis - C7 | 402228 | Scaled Integer Format (10000 = 100%)
28 | 8 | Molar Analysis - C8 | 402229 | Scaled Integer Format (10000 = 100%)
29 | 8 | Molar Analysis - C9 | 402230 | Scaled Integer Format (10000 = 100%)
30 | 8 | Molar Analysis - C10 | 402231 | Scaled Integer Format (10000 = 100%)
31 | 8 | Molar Analysis - He | 402232 | Scaled Integer Format (10000 = 100%)
32 | 8 | Molar Analysis - Ar | 402233 | Scaled Integer Format (10000 = 100%)
33 | 8 | Molar Analysis - C5 (neo-p) | 402234 | Scaled Integer Format (10000 = 100%)
34 | 8 | Molar Analysis - Ux | 402235 | Scaled Integer Format (10000 = 100%)
35 | 8 | Molar Analysis - Uy | 402236 | Scaled Integer Format (10000 = 100%)
36 | 8 | Meter Signals - Reserved | 402237
37 | 8 | Meter Signals - Reserved | 402238
38 | 8 | Meter Signals - Reserved | 402239
39 | 8 | Meter Signals - Reserved | 402240
40 | 8 | Meter Signals - Reset Acc 1 | 402241
41 | 8 | Meter Signals - Reset Acc 2 | 402242
42 | 8 | Meter Signals - Reset Acc 3 | 402243
43 | 8 | Meter Signals - Reset Acc 4 | 402244
44 | 8 | Write Daily Archive | 402245
45 | 8 | Write Hourly Archive | 402246
46 | 8 | Meter Signals - Reserved | 402247
47 | 8 | Meter Signals - Reserved | 402248
48 | 8 | Meter Signals - Reserved | 402249
49 | 8 | Meter Signals - Reserved | 402250
50 | 8 | Meter Signals - Reserved | 402251
51 | 8 | Meter Signals - Reserved | 402252
52 | 8 | Analysis is Present | 402253
53 | 8 | Meter Archive Record Fetch | 402254 | (=0 signal not present)
54 | 8 | Meter Archive Record Age | 402255 | (=0 current)
55 | 8 | Meter Archive File Select | 402256 | (=0 daily, 1=hourly)
Meter 9 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Meter Disable | 402401
1 | 9 | Water % | 402402 | Scaled Integer Format
2 | 9 | Temperature | 402403 | Floating Point Format
3 | 9 | Temperature | 402404 | Floating Point Format
4 | 9 | Pressure | 402405 | Floating Point Format
5 | 9 | Pressure | 402406 | Floating Point Format
6 | 9 | Differential Pressure | 402407 | Floating Point Format
7 | 9 | Differential Pressure | 402408 | Floating Point Format
8 | 9 | Density | 402409 | Floating Point Format
9 | 9 | Density | 402410 | Floating Point Format
10 | 9 | Reserved | 402411
11 | 9 | Reserved | 402412
12 | 9 | Molar Analysis - C1 | 402413 | Scaled Integer Format (10000 = 100%)
13 | 9 | Molar Analysis - N2 | 402414 | Scaled Integer Format (10000 = 100%)
14 | 9 | Molar Analysis - CO2 | 402415 | Scaled Integer Format (10000 = 100%)
15 | 9 | Molar Analysis - C2 | 402416 | Scaled Integer Format (10000 = 100%)
16 | 9 | Molar Analysis - C3 | 402417 | Scaled Integer Format (10000 = 100%)
17 | 9 | Molar Analysis - H2O | 402418 | Scaled Integer Format (10000 = 100%)
18 | 9 | Molar Analysis - H2S | 402419 | Scaled Integer Format (10000 = 100%)
19 | 9 | Molar Analysis - H2 | 402420 | Scaled Integer Format (10000 = 100%)
20 | 9 | Molar Analysis - CO | 402421 | Scaled Integer Format (10000 = 100%)
21 | 9 | Molar Analysis - O2 | 402422 | Scaled Integer Format (10000 = 100%)
22 | 9 | Molar Analysis - iC4 | 402423 | Scaled Integer Format (10000 = 100%)
23 | 9 | Molar Analysis - C4 | 402424 | Scaled Integer Format (10000 = 100%)
24 | 9 | Molar Analysis - iC5 | 402425 | Scaled Integer Format (10000 = 100%)
25 | 9 | Molar Analysis - C5 | 402426 | Scaled Integer Format (10000 = 100%)
26 | 9 | Molar Analysis - C6 | 402427 | Scaled Integer Format (10000 = 100%)
27 | 9 | Molar Analysis - C7 | 402428 | Scaled Integer Format (10000 = 100%)
28 | 9 | Molar Analysis - C8 | 402429 | Scaled Integer Format (10000 = 100%)
29 | 9 | Molar Analysis - C9 | 402430 | Scaled Integer Format (10000 = 100%)
30 | 9 | Molar Analysis - C10 | 402431 | Scaled Integer Format (10000 = 100%)
31 | 9 | Molar Analysis - He | 402432 | Scaled Integer Format (10000 = 100%)
32 | 9 | Molar Analysis - Ar | 402433 | Scaled Integer Format (10000 = 100%)
33 | 9 | Molar Analysis - C5 (neo-p) | 402434 | Scaled Integer Format (10000 = 100%)
34 | 9 | Molar Analysis - Ux | 402435 | Scaled Integer Format (10000 = 100%)
35 | 9 | Molar Analysis - Uy | 402436 | Scaled Integer Format (10000 = 100%)
36 | 9 | Meter Signals - Reserved | 402437
37 | 9 | Meter Signals - Reserved | 402438
38 | 9 | Meter Signals - Reserved | 402439
39 | 9 | Meter Signals - Reserved | 402440
40 | 9 | Meter Signals - Reset Acc 1 | 402441
41 | 9 | Meter Signals - Reset Acc 2 | 402442
42 | 9 | Meter Signals - Reset Acc 3 | 402443
43 | 9 | Meter Signals - Reset Acc 4 | 402444
44 | 9 | Write Daily Archive | 402445
45 | 9 | Write Hourly Archive | 402446
46 | 9 | Meter Signals - Reserved | 402447
47 | 9 | Meter Signals - Reserved | 402448
48 | 9 | Meter Signals - Reserved | 402449
49 | 9 | Meter Signals - Reserved | 402450
50 | 9 | Meter Signals - Reserved | 402451
51 | 9 | Meter Signals - Reserved | 402452
52 | 9 | Analysis is Present | 402453
53 | 9 | Meter Archive Record Fetch | 402454 | (=0 signal not present)
54 | 9 | Meter Archive Record Age | 402455 | (=0 current)
55 | 9 | Meter Archive File Select | 402456 | (=0 daily, 1=hourly)
Meter 10 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Meter Disable | 402601
1 | 10 | Water % | 402602 | Scaled Integer Format
2 | 10 | Temperature | 402603 | Floating Point Format
3 | 10 | Temperature | 402604 | Floating Point Format
4 | 10 | Pressure | 402605 | Floating Point Format
5 | 10 | Pressure | 402606 | Floating Point Format
6 | 10 | Differential Pressure | 402607 | Floating Point Format
7 | 10 | Differential Pressure | 402608 | Floating Point Format
8 | 10 | Density | 402609 | Floating Point Format
9 | 10 | Density | 402610 | Floating Point Format
10 | 10 | Reserved | 402611
11 | 10 | Reserved | 402612
12 | 10 | Molar Analysis - C1 | 402613 | Scaled Integer Format (10000 = 100%)
13 | 10 | Molar Analysis - N2 | 402614 | Scaled Integer Format (10000 = 100%)
14 | 10 | Molar Analysis - CO2 | 402615 | Scaled Integer Format (10000 = 100%)
15 | 10 | Molar Analysis - C2 | 402616 | Scaled Integer Format (10000 = 100%)
16 | 10 | Molar Analysis - C3 | 402617 | Scaled Integer Format (10000 = 100%)
17 | 10 | Molar Analysis - H2O | 402618 | Scaled Integer Format (10000 = 100%)
18 | 10 | Molar Analysis - H2S | 402619 | Scaled Integer Format (10000 = 100%)
19 | 10 | Molar Analysis - H2 | 402620 | Scaled Integer Format (10000 = 100%)
20 | 10 | Molar Analysis - CO | 402621 | Scaled Integer Format (10000 = 100%)
21 | 10 | Molar Analysis - O2 | 402622 | Scaled Integer Format (10000 = 100%)
22 | 10 | Molar Analysis - iC4 | 402623 | Scaled Integer Format (10000 = 100%)
23 | 10 | Molar Analysis - C4 | 402624 | Scaled Integer Format (10000 = 100%)
24 | 10 | Molar Analysis - iC5 | 402625 | Scaled Integer Format (10000 = 100%)
25 | 10 | Molar Analysis - C5 | 402626 | Scaled Integer Format (10000 = 100%)
26 | 10 | Molar Analysis - C6 | 402627 | Scaled Integer Format (10000 = 100%)
27 | 10 | Molar Analysis - C7 | 402628 | Scaled Integer Format (10000 = 100%)
28 | 10 | Molar Analysis - C8 | 402629 | Scaled Integer Format (10000 = 100%)
29 | 10 | Molar Analysis - C9 | 402630 | Scaled Integer Format (10000 = 100%)
30 | 10 | Molar Analysis - C10 | 402631 | Scaled Integer Format (10000 = 100%)
31 | 10 | Molar Analysis - He | 402632 | Scaled Integer Format (10000 = 100%)
32 | 10 | Molar Analysis - Ar | 402633 | Scaled Integer Format (10000 = 100%)
33 | 10 | Molar Analysis - C5 (neo-p) | 402634 | Scaled Integer Format (10000 = 100%)
34 | 10 | Molar Analysis - Ux | 402635 | Scaled Integer Format (10000 = 100%)
35 | 10 | Molar Analysis - Uy | 402636 | Scaled Integer Format (10000 = 100%)
36 | 10 | Meter Signals - Reserved | 402637
37 | 10 | Meter Signals - Reserved | 402638
38 | 10 | Meter Signals - Reserved | 402639
39 | 10 | Meter Signals - Reserved | 402640
40 | 10 | Meter Signals - Reset Acc 1 | 402641
41 | 10 | Meter Signals - Reset Acc 2 | 402642
42 | 10 | Meter Signals - Reset Acc 3 | 402643
43 | 10 | Meter Signals - Reset Acc 4 | 402644
44 | 10 | Write Daily Archive | 402645
45 | 10 | Write Hourly Archive | 402646
46 | 10 | Meter Signals - Reserved | 402647
47 | 10 | Meter Signals - Reserved | 402648
48 | 10 | Meter Signals - Reserved | 402649
49 | 10 | Meter Signals - Reserved | 402650
50 | 10 | Meter Signals - Reserved | 402651
51 | 10 | Meter Signals - Reserved | 402652
52 | 10 | Analysis is Present | 402653
53 | 10 | Meter Archive Record Fetch | 402654 | (=0 signal not present)
54 | 10 | Meter Archive Record Age | 402655 | (=0 current)
55 | 10 | Meter Archive File Select | 402656 | (=0 daily, 1=hourly)
Meter 11 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Meter Disable | 402801
1 | 11 | Water % | 402802 | Scaled Integer Format
2 | 11 | Temperature | 402803 | Floating Point Format
3 | 11 | Temperature | 402804 | Floating Point Format
4 | 11 | Pressure | 402805 | Floating Point Format
5 | 11 | Pressure | 402806 | Floating Point Format
6 | 11 | Differential Pressure | 402807 | Floating Point Format
7 | 11 | Differential Pressure | 402808 | Floating Point Format
8 | 11 | Density | 402809 | Floating Point Format
9 | 11 | Density | 402810 | Floating Point Format
10 | 11 | Reserved | 402811
11 | 11 | Reserved | 402812
12 | 11 | Molar Analysis - C1 | 402813 | Scaled Integer Format (10000 = 100%)
13 | 11 | Molar Analysis - N2 | 402814 | Scaled Integer Format (10000 = 100%)
14 | 11 | Molar Analysis - CO2 | 402815 | Scaled Integer Format (10000 = 100%)
15 | 11 | Molar Analysis - C2 | 402816 | Scaled Integer Format (10000 = 100%)
16 | 11 | Molar Analysis - C3 | 402817 | Scaled Integer Format (10000 = 100%)
17 | 11 | Molar Analysis - H2O | 402818 | Scaled Integer Format (10000 = 100%)
18 | 11 | Molar Analysis - H2S | 402819 | Scaled Integer Format (10000 = 100%)
19 | 11 | Molar Analysis - H2 | 402820 | Scaled Integer Format (10000 = 100%)
20 | 11 | Molar Analysis - CO | 402821 | Scaled Integer Format (10000 = 100%)
21 | 11 | Molar Analysis - O2 | 402822 | Scaled Integer Format (10000 = 100%)
22 | 11 | Molar Analysis - iC4 | 402823 | Scaled Integer Format (10000 = 100%)
23 | 11 | Molar Analysis - C4 | 402824 | Scaled Integer Format (10000 = 100%)
24 | 11 | Molar Analysis - iC5 | 402825 | Scaled Integer Format (10000 = 100%)
25 | 11 | Molar Analysis - C5 | 402826 | Scaled Integer Format (10000 = 100%)
26 | 11 | Molar Analysis - C6 | 402827 | Scaled Integer Format (10000 = 100%)
27 | 11 | Molar Analysis - C7 | 402828 | Scaled Integer Format (10000 = 100%)
28 | 11 | Molar Analysis - C8 | 402829 | Scaled Integer Format (10000 = 100%)
29 | 11 | Molar Analysis - C9 | 402830 | Scaled Integer Format (10000 = 100%)
30 | 11 | Molar Analysis - C10 | 402831 | Scaled Integer Format (10000 = 100%)
31 | 11 | Molar Analysis - He | 402832 | Scaled Integer Format (10000 = 100%)
32 | 11 | Molar Analysis - Ar | 402833 | Scaled Integer Format (10000 = 100%)
33 | 11 | Molar Analysis - C5 (neo-p) | 402834 | Scaled Integer Format (10000 = 100%)
34 | 11 | Molar Analysis - Ux | 402835 | Scaled Integer Format (10000 = 100%)
35 | 11 | Molar Analysis - Uy | 402836 | Scaled Integer Format (10000 = 100%)
36 | 11 | Meter Signals - Reserved | 402837
37 | 11 | Meter Signals - Reserved | 402838
38 | 11 | Meter Signals - Reserved | 402839
39 | 11 | Meter Signals - Reserved | 402840
40 | 11 | Meter Signals - Reset Acc 1 | 402841
41 | 11 | Meter Signals - Reset Acc 2 | 402842
42 | 11 | Meter Signals - Reset Acc 3 | 402843
43 | 11 | Meter Signals - Reset Acc 4 | 402844
44 | 11 | Write Daily Archive | 402845
45 | 11 | Write Hourly Archive | 402846
46 | 11 | Meter Signals - Reserved | 402847
47 | 11 | Meter Signals - Reserved | 402848
48 | 11 | Meter Signals - Reserved | 402849
49 | 11 | Meter Signals - Reserved | 402850
50 | 11 | Meter Signals - Reserved | 402851
51 | 11 | Meter Signals - Reserved | 402852
52 | 11 | Analysis is Present | 402853
53 | 11 | Meter Archive Record Fetch | 402854 | (=0 signal not present)
54 | 11 | Meter Archive Record Age | 402855 | (=0 current)
55 | 11 | Meter Archive File Select | 402856 | (=0 daily, 1=hourly)
Meter 12 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Meter Disable | 403001
1 | 12 | Water % | 403002 | Scaled Integer Format
2 | 12 | Temperature | 403003 | Floating Point Format
3 | 12 | Temperature | 403004 | Floating Point Format
4 | 12 | Pressure | 403005 | Floating Point Format
5 | 12 | Pressure | 403006 | Floating Point Format
6 | 12 | Differential Pressure | 403007 | Floating Point Format
7 | 12 | Differential Pressure | 403008 | Floating Point Format
8 | 12 | Density | 403009 | Floating Point Format
9 | 12 | Density | 403010 | Floating Point Format
10 | 12 | Reserved | 403011
11 | 12 | Reserved | 403012
12 | 12 | Molar Analysis - C1 | 403013 | Scaled Integer Format (10000 = 100%)
13 | 12 | Molar Analysis - N2 | 403014 | Scaled Integer Format (10000 = 100%)
14 | 12 | Molar Analysis - CO2 | 403015 | Scaled Integer Format (10000 = 100%)
15 | 12 | Molar Analysis - C2 | 403016 | Scaled Integer Format (10000 = 100%)
16 | 12 | Molar Analysis - C3 | 403017 | Scaled Integer Format (10000 = 100%)
17 | 12 | Molar Analysis - H2O | 403018 | Scaled Integer Format (10000 = 100%)
18 | 12 | Molar Analysis - H2S | 403019 | Scaled Integer Format (10000 = 100%)
19 | 12 | Molar Analysis - H2 | 403020 | Scaled Integer Format (10000 = 100%)
20 | 12 | Molar Analysis - CO | 403021 | Scaled Integer Format (10000 = 100%)
21 | 12 | Molar Analysis - O2 | 403022 | Scaled Integer Format (10000 = 100%)
22 | 12 | Molar Analysis - iC4 | 403023 | Scaled Integer Format (10000 = 100%)
23 | 12 | Molar Analysis - C4 | 403024 | Scaled Integer Format (10000 = 100%)
24 | 12 | Molar Analysis - iC5 | 403025 | Scaled Integer Format (10000 = 100%)
25 | 12 | Molar Analysis - C5 | 403026 | Scaled Integer Format (10000 = 100%)
26 | 12 | Molar Analysis - C6 | 403027 | Scaled Integer Format (10000 = 100%)
27 | 12 | Molar Analysis - C7 | 403028 | Scaled Integer Format (10000 = 100%)
28 | 12 | Molar Analysis - C8 | 403029 | Scaled Integer Format (10000 = 100%)
29 | 12 | Molar Analysis - C9 | 403030 | Scaled Integer Format (10000 = 100%)
30 | 12 | Molar Analysis - C10 | 403031 | Scaled Integer Format (10000 = 100%)
31 | 12 | Molar Analysis - He | 403032 | Scaled Integer Format (10000 = 100%)
32 | 12 | Molar Analysis - Ar | 403033 | Scaled Integer Format (10000 = 100%)
33 | 12 | Molar Analysis - C5 (neo-p) | 403034 | Scaled Integer Format (10000 = 100%)
34 | 12 | Molar Analysis - Ux | 403035 | Scaled Integer Format (10000 = 100%)
35 | 12 | Molar Analysis - Uy | 403036 | Scaled Integer Format (10000 = 100%)
36 | 12 | Meter Signals - Reserved | 403037
37 | 12 | Meter Signals - Reserved | 403038
38 | 12 | Meter Signals - Reserved | 403039
39 | 12 | Meter Signals - Reserved | 403040
40 | 12 | Meter Signals - Reset Acc 1 | 403041
41 | 12 | Meter Signals - Reset Acc 2 | 403042
42 | 12 | Meter Signals - Reset Acc 3 | 403043
43 | 12 | Meter Signals - Reset Acc 4 | 403044
44 | 12 | Write Daily Archive | 403045
45 | 12 | Write Hourly Archive | 403046
46 | 12 | Meter Signals - Reserved | 403047
47 | 12 | Meter Signals - Reserved | 403048
48 | 12 | Meter Signals - Reserved | 403049
49 | 12 | Meter Signals - Reserved | 403050
50 | 12 | Meter Signals - Reserved | 403051
51 | 12 | Meter Signals - Reserved | 403052
52 | 12 | Analysis is Present | 403053
53 | 12 | Meter Archive Record Fetch | 403054 | (=0 signal not present)
54 | 12 | Meter Archive Record Age | 403055 | (=0 current)
55 | 12 | Meter Archive File Select | 403056 | (=0 daily, 1=hourly)
Meter 13 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Meter Disable | 403201
1 | 13 | Water % | 403202 | Scaled Integer Format
2 | 13 | Temperature | 403203 | Floating Point Format
3 | 13 | Temperature | 403204 | Floating Point Format
4 | 13 | Pressure | 403205 | Floating Point Format
5 | 13 | Pressure | 403206 | Floating Point Format
6 | 13 | Differential Pressure | 403207 | Floating Point Format
7 | 13 | Differential Pressure | 403208 | Floating Point Format
8 | 13 | Density | 403209 | Floating Point Format
9 | 13 | Density | 403210 | Floating Point Format
10 | 13 | Reserved | 403211
11 | 13 | Reserved | 403212
12 | 13 | Molar Analysis - C1 | 403213 | Scaled Integer Format (10000 = 100%)
13 | 13 | Molar Analysis - N2 | 403214 | Scaled Integer Format (10000 = 100%)
14 | 13 | Molar Analysis - CO2 | 403215 | Scaled Integer Format (10000 = 100%)
15 | 13 | Molar Analysis - C2 | 403216 | Scaled Integer Format (10000 = 100%)
16 | 13 | Molar Analysis - C3 | 403217 | Scaled Integer Format (10000 = 100%)
17 | 13 | Molar Analysis - H2O | 403218 | Scaled Integer Format (10000 = 100%)
18 | 13 | Molar Analysis - H2S | 403219 | Scaled Integer Format (10000 = 100%)
19 | 13 | Molar Analysis - H2 | 403220 | Scaled Integer Format (10000 = 100%)
20 | 13 | Molar Analysis - CO | 403221 | Scaled Integer Format (10000 = 100%)
21 | 13 | Molar Analysis - O2 | 403222 | Scaled Integer Format (10000 = 100%)
22 | 13 | Molar Analysis - iC4 | 403223 | Scaled Integer Format (10000 = 100%)
23 | 13 | Molar Analysis - C4 | 403224 | Scaled Integer Format (10000 = 100%)
24 | 13 | Molar Analysis - iC5 | 403225 | Scaled Integer Format (10000 = 100%)
25 | 13 | Molar Analysis - C5 | 403226 | Scaled Integer Format (10000 = 100%)
26 | 13 | Molar Analysis - C6 | 403227 | Scaled Integer Format (10000 = 100%)
27 | 13 | Molar Analysis - C7 | 403228 | Scaled Integer Format (10000 = 100%)
28 | 13 | Molar Analysis - C8 | 403229 | Scaled Integer Format (10000 = 100%)
29 | 13 | Molar Analysis - C9 | 403230 | Scaled Integer Format (10000 = 100%)
30 | 13 | Molar Analysis - C10 | 403231 | Scaled Integer Format (10000 = 100%)
31 | 13 | Molar Analysis - He | 403232 | Scaled Integer Format (10000 = 100%)
32 | 13 | Molar Analysis - Ar | 403233 | Scaled Integer Format (10000 = 100%)
33 | 13 | Molar Analysis - C5 (neo-p) | 403234 | Scaled Integer Format (10000 = 100%)
34 | 13 | Molar Analysis - Ux | 403235 | Scaled Integer Format (10000 = 100%)
35 | 13 | Molar Analysis - Uy | 403236 | Scaled Integer Format (10000 = 100%)
36 | 13 | Meter Signals - Reserved | 403237
37 | 13 | Meter Signals - Reserved | 403238
38 | 13 | Meter Signals - Reserved | 403239
39 | 13 | Meter Signals - Reserved | 403240
40 | 13 | Meter Signals - Reset Acc 1 | 403241
41 | 13 | Meter Signals - Reset Acc 2 | 403242
42 | 13 | Meter Signals - Reset Acc 3 | 403243
43 | 13 | Meter Signals - Reset Acc 4 | 403244
44 | 13 | Write Daily Archive | 403245
45 | 13 | Write Hourly Archive | 403246
46 | 13 | Meter Signals - Reserved | 403247
47 | 13 | Meter Signals - Reserved | 403248
48 | 13 | Meter Signals - Reserved | 403249
49 | 13 | Meter Signals - Reserved | 403250
50 | 13 | Meter Signals - Reserved | 403251
51 | 13 | Meter Signals - Reserved | 403252
52 | 13 | Analysis is Present | 403253
53 | 13 | Meter Archive Record Fetch | 403254 | (=0 signal not present)
54 | 13 | Meter Archive Record Age | 403255 | (=0 current)
55 | 13 | Meter Archive File Select | 403256 | (=0 daily, 1=hourly)
Meter 14 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Meter Disable | 403401
1 | 14 | Water % | 403402 | Scaled Integer Format
2 | 14 | Temperature | 403403 | Floating Point Format
3 | 14 | Temperature | 403404 | Floating Point Format
4 | 14 | Pressure | 403405 | Floating Point Format
5 | 14 | Pressure | 403406 | Floating Point Format
6 | 14 | Differential Pressure | 403407 | Floating Point Format
7 | 14 | Differential Pressure | 403408 | Floating Point Format
8 | 14 | Density | 403409 | Floating Point Format
9 | 14 | Density | 403410 | Floating Point Format
10 | 14 | Reserved | 403411
11 | 14 | Reserved | 403412
12 | 14 | Molar Analysis - C1 | 403413 | Scaled Integer Format (10000 = 100%)
13 | 14 | Molar Analysis - N2 | 403414 | Scaled Integer Format (10000 = 100%)
14 | 14 | Molar Analysis - CO2 | 403415 | Scaled Integer Format (10000 = 100%)
15 | 14 | Molar Analysis - C2 | 403416 | Scaled Integer Format (10000 = 100%)
16 | 14 | Molar Analysis - C3 | 403417 | Scaled Integer Format (10000 = 100%)
17 | 14 | Molar Analysis - H2O | 403418 | Scaled Integer Format (10000 = 100%)
18 | 14 | Molar Analysis - H2S | 403419 | Scaled Integer Format (10000 = 100%)
19 | 14 | Molar Analysis - H2 | 403420 | Scaled Integer Format (10000 = 100%)
20 | 14 | Molar Analysis - CO | 403421 | Scaled Integer Format (10000 = 100%)
21 | 14 | Molar Analysis - O2 | 403422 | Scaled Integer Format (10000 = 100%)
22 | 14 | Molar Analysis - iC4 | 403423 | Scaled Integer Format (10000 = 100%)
23 | 14 | Molar Analysis - C4 | 403424 | Scaled Integer Format (10000 = 100%)
24 | 14 | Molar Analysis - iC5 | 403425 | Scaled Integer Format (10000 = 100%)
25 | 14 | Molar Analysis - C5 | 403426 | Scaled Integer Format (10000 = 100%)
26 | 14 | Molar Analysis - C6 | 403427 | Scaled Integer Format (10000 = 100%)
27 | 14 | Molar Analysis - C7 | 403428 | Scaled Integer Format (10000 = 100%)
28 | 14 | Molar Analysis - C8 | 403429 | Scaled Integer Format (10000 = 100%)
29 | 14 | Molar Analysis - C9 | 403430 | Scaled Integer Format (10000 = 100%)
30 | 14 | Molar Analysis - C10 | 403431 | Scaled Integer Format (10000 = 100%)
31 | 14 | Molar Analysis - He | 403432 | Scaled Integer Format (10000 = 100%)
32 | 14 | Molar Analysis - Ar | 403433 | Scaled Integer Format (10000 = 100%)
33 | 14 | Molar Analysis - C5 (neo-p) | 403434 | Scaled Integer Format (10000 = 100%)
34 | 14 | Molar Analysis - Ux | 403435 | Scaled Integer Format (10000 = 100%)
35 | 14 | Molar Analysis - Uy | 403436 | Scaled Integer Format (10000 = 100%)
36 | 14 | Meter Signals - Reserved | 403437
37 | 14 | Meter Signals - Reserved | 403438
38 | 14 | Meter Signals - Reserved | 403439
39 | 14 | Meter Signals - Reserved | 403440
40 | 14 | Meter Signals - Reset Acc 1 | 403441
41 | 14 | Meter Signals - Reset Acc 2 | 403442
42 | 14 | Meter Signals - Reset Acc 3 | 403443
43 | 14 | Meter Signals - Reset Acc 4 | 403444
44 | 14 | Write Daily Archive | 403445
45 | 14 | Write Hourly Archive | 403446
46 | 14 | Meter Signals - Reserved | 403447
47 | 14 | Meter Signals - Reserved | 403448
48 | 14 | Meter Signals - Reserved | 403449
49 | 14 | Meter Signals - Reserved | 403450
50 | 14 | Meter Signals - Reserved | 403451
51 | 14 | Meter Signals - Reserved | 403452
52 | 14 | Analysis is Present | 403453
53 | 14 | Meter Archive Record Fetch | 403454 | (=0 signal not present)
54 | 14 | Meter Archive Record Age | 403455 | (=0 current)
55 | 14 | Meter Archive File Select | 403456 | (=0 daily, 1=hourly)
Meter 15 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Meter Disable | 403601
1 | 15 | Water % | 403602 | Scaled Integer Format
2 | 15 | Temperature | 403603 | Floating Point Format
3 | 15 | Temperature | 403604 | Floating Point Format
4 | 15 | Pressure | 403605 | Floating Point Format
5 | 15 | Pressure | 403606 | Floating Point Format
6 | 15 | Differential Pressure | 403607 | Floating Point Format
7 | 15 | Differential Pressure | 403608 | Floating Point Format
8 | 15 | Density | 403609 | Floating Point Format
9 | 15 | Density | 403610 | Floating Point Format
10 | 15 | Reserved | 403611
11 | 15 | Reserved | 403612
12 | 15 | Molar Analysis - C1 | 403613 | Scaled Integer Format (10000 = 100%)
13 | 15 | Molar Analysis - N2 | 403614 | Scaled Integer Format (10000 = 100%)
14 | 15 | Molar Analysis - CO2 | 403615 | Scaled Integer Format (10000 = 100%)
15 | 15 | Molar Analysis - C2 | 403616 | Scaled Integer Format (10000 = 100%)
16 | 15 | Molar Analysis - C3 | 403617 | Scaled Integer Format (10000 = 100%)
17 | 15 | Molar Analysis - H2O | 403618 | Scaled Integer Format (10000 = 100%)
18 | 15 | Molar Analysis - H2S | 403619 | Scaled Integer Format (10000 = 100%)
19 | 15 | Molar Analysis - H2 | 403620 | Scaled Integer Format (10000 = 100%)
20 | 15 | Molar Analysis - CO | 403621 | Scaled Integer Format (10000 = 100%)
21 | 15 | Molar Analysis - O2 | 403622 | Scaled Integer Format (10000 = 100%)
22 | 15 | Molar Analysis - iC4 | 403623 | Scaled Integer Format (10000 = 100%)
23 | 15 | Molar Analysis - C4 | 403624 | Scaled Integer Format (10000 = 100%)
24 | 15 | Molar Analysis - iC5 | 403625 | Scaled Integer Format (10000 = 100%)
25 | 15 | Molar Analysis - C5 | 403626 | Scaled Integer Format (10000 = 100%)
26 | 15 | Molar Analysis - C6 | 403627 | Scaled Integer Format (10000 = 100%)
27 | 15 | Molar Analysis - C7 | 403628 | Scaled Integer Format (10000 = 100%)
28 | 15 | Molar Analysis - C8 | 403629 | Scaled Integer Format (10000 = 100%)
29 | 15 | Molar Analysis - C9 | 403630 | Scaled Integer Format (10000 = 100%)
30 | 15 | Molar Analysis - C10 | 403631 | Scaled Integer Format (10000 = 100%)
31 | 15 | Molar Analysis - He | 403632 | Scaled Integer Format (10000 = 100%)
32 | 15 | Molar Analysis - Ar | 403633 | Scaled Integer Format (10000 = 100%)
33 | 15 | Molar Analysis - C5 (neo-p) | 403634 | Scaled Integer Format (10000 = 100%)
34 | 15 | Molar Analysis - Ux | 403635 | Scaled Integer Format (10000 = 100%)
35 | 15 | Molar Analysis - Uy | 403636 | Scaled Integer Format (10000 = 100%)
36 | 15 | Meter Signals - Reserved | 403637
37 | 15 | Meter Signals - Reserved | 403638
38 | 15 | Meter Signals - Reserved | 403639
39 | 15 | Meter Signals - Reserved | 403640
40 | 15 | Meter Signals - Reset Acc 1 | 403641
41 | 15 | Meter Signals - Reset Acc 2 | 403642
42 | 15 | Meter Signals - Reset Acc 3 | 403643
43 | 15 | Meter Signals - Reset Acc 4 | 403644
44 | 15 | Write Daily Archive | 403645
45 | 15 | Write Hourly Archive | 403646
46 | 15 | Meter Signals - Reserved | 403647
47 | 15 | Meter Signals - Reserved | 403648
48 | 15 | Meter Signals - Reserved | 403649
49 | 15 | Meter Signals - Reserved | 403650
50 | 15 | Meter Signals - Reserved | 403651
51 | 15 | Meter Signals - Reserved | 403652
52 | 15 | Analysis is Present | 403653
53 | 15 | Meter Archive Record Fetch | 403654 | (=0 signal not present)
54 | 15 | Meter Archive Record Age | 403655 | (=0 current)
55 | 15 | Meter Archive File Select | 403656 | (=0 daily, 1=hourly)
Meter 16 Variables Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Meter Disable | 403801
1 | 16 | Water % | 403802 | Scaled Integer Format
2 | 16 | Temperature | 403803 | Floating Point Format
3 | 16 | Temperature | 403804 | Floating Point Format
4 | 16 | Pressure | 403805 | Floating Point Format
5 | 16 | Pressure | 403806 | Floating Point Format
6 | 16 | Differential Pressure | 403807 | Floating Point Format
7 | 16 | Differential Pressure | 403808 | Floating Point Format
8 | 16 | Density | 403809 | Floating Point Format
9 | 16 | Density | 403810 | Floating Point Format
10 | 16 | Reserved | 403811
11 | 16 | Reserved | 403812
12 | 16 | Molar Analysis - C1 | 403813 | Scaled Integer Format (10000 = 100%)
13 | 16 | Molar Analysis - N2 | 403814 | Scaled Integer Format (10000 = 100%)
14 | 16 | Molar Analysis - CO2 | 403815 | Scaled Integer Format (10000 = 100%)
15 | 16 | Molar Analysis - C2 | 403816 | Scaled Integer Format (10000 = 100%)
16 | 16 | Molar Analysis - C3 | 403817 | Scaled Integer Format (10000 = 100%)
17 | 16 | Molar Analysis - H2O | 403818 | Scaled Integer Format (10000 = 100%)
18 | 16 | Molar Analysis - H2S | 403819 | Scaled Integer Format (10000 = 100%)
19 | 16 | Molar Analysis - H2 | 403820 | Scaled Integer Format (10000 = 100%)
20 | 16 | Molar Analysis - CO | 403821 | Scaled Integer Format (10000 = 100%)
21 | 16 | Molar Analysis - O2 | 403822 | Scaled Integer Format (10000 = 100%)
22 | 16 | Molar Analysis - iC4 | 403823 | Scaled Integer Format (10000 = 100%)
23 | 16 | Molar Analysis - C4 | 403824 | Scaled Integer Format (10000 = 100%)
24 | 16 | Molar Analysis - iC5 | 403825 | Scaled Integer Format (10000 = 100%)
25 | 16 | Molar Analysis - C5 | 403826 | Scaled Integer Format (10000 = 100%)
26 | 16 | Molar Analysis - C6 | 403827 | Scaled Integer Format (10000 = 100%)
27 | 16 | Molar Analysis - C7 | 403828 | Scaled Integer Format (10000 = 100%)
28 | 16 | Molar Analysis - C8 | 403829 | Scaled Integer Format (10000 = 100%)
29 | 16 | Molar Analysis - C9 | 403830 | Scaled Integer Format (10000 = 100%)
30 | 16 | Molar Analysis - C10 | 403831 | Scaled Integer Format (10000 = 100%)
31 | 16 | Molar Analysis - He | 403832 | Scaled Integer Format (10000 = 100%)
32 | 16 | Molar Analysis - Ar | 403833 | Scaled Integer Format (10000 = 100%)
33 | 16 | Molar Analysis - C5 (neo-p) | 403834 | Scaled Integer Format (10000 = 100%)
34 | 16 | Molar Analysis - Ux | 403835 | Scaled Integer Format (10000 = 100%)
35 | 16 | Molar Analysis - Uy | 403836 | Scaled Integer Format (10000 = 100%)
36 | 16 | Meter Signals - Reserved | 403837
37 | 16 | Meter Signals - Reserved | 403838
38 | 16 | Meter Signals - Reserved | 403839
39 | 16 | Meter Signals - Reserved | 403840
40 | 16 | Meter Signals - Reset Acc 1 | 403841
41 | 16 | Meter Signals - Reset Acc 2 | 403842
42 | 16 | Meter Signals - Reset Acc 3 | 403843
43 | 16 | Meter Signals - Reset Acc 4 | 403844
44 | 16 | Write Daily Archive | 403845
45 | 16 | Write Hourly Archive | 403846
46 | 16 | Meter Signals - Reserved | 403847
47 | 16 | Meter Signals - Reserved | 403848
48 | 16 | Meter Signals - Reserved | 403849
49 | 16 | Meter Signals - Reserved | 403850
50 | 16 | Meter Signals - Reserved | 403851
51 | 16 | Meter Signals - Reserved | 403852
52 | 16 | Analysis is Present | 403853
53 | 16 | Meter Archive Record Fetch | 403854 | (=0 signal not present)
54 | 16 | Meter Archive Record Age | 403855 | (=0 current)
55 | 16 | Meter Archive File Select | 403856 | (=0 daily, 1=hourly)

## Meter Results - Orifice & Liq
Meter 1 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Scan Count: process input | 400901
1 | 1 | Scan Count: calculation | 400902
2 | 1 | Meter in Alarm | 400903 | 0=no alarm
3 | 1 | Reserved | 400904
4 | 1 | Net Accumulator | 400905 | Long Integer Format
5 | 1 | Net Accumulator | 400906 | Long Integer Format
6 | 1 | Net Flow Rate | 400907 | Floating Point Format
7 | 1 | Net Flow Rate | 400908 | Floating Point Format
8 | 1 | Gross Accumulator | 400909 | Long Integer Format
9 | 1 | Gross Accumulator | 400910 | Long Integer Format
10 | 1 | Gross Standard Accumulator | 400911 | Long Integer Format
11 | 1 | Gross Standard Accumulator | 400912 | Long Integer Format
12 | 1 | Mass Accumulator | 400913 | Long Integer Format
13 | 1 | Mass Accumulator | 400914 | Long Integer Format
14 | 1 | Reserved | 400915
15 | 1 | Reserved | 400916
16 | 1 | Reserved | 400917
17 | 1 | Reserved | 400918
18 | 1 | Reserved | 400919
19 | 1 | Reserved | 400920
20 | 1 | Reserved | 400921
21 | 1 | Reserved | 400922
22 | 1 | Reserved | 400923
23 | 1 | Reserved | 400924
24 | 1 | Reserved | 400925
25 | 1 | Reserved | 400926
26 | 1 | Reserved | 400927
27 | 1 | Reserved | 400928
28 | 1 | Reserved | 400929
29 | 1 | Reserved | 400930
30 | 1 | Reserved | 400931
31 | 1 | Reserved | 400932
32 | 1 | Reserved | 400933
33 | 1 | Reserved | 400934
34 | 1 | Reserved | 400935
35 | 1 | Reserved | 400936
36 | 1 | Reserved | 400937
37 | 1 | Reserved | 400938
Meter 2 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Scan Count: process input | 401101
1 | 2 | Scan Count: calculation | 401102
2 | 2 | Meter in Alarm | 401103 | 0=no alarm
3 | 2 | Reserved | 401104
4 | 2 | Net Accumulator | 401105 | Long Integer Format
5 | 2 | Net Accumulator | 401106 | Long Integer Format
6 | 2 | Net Flow Rate | 401107 | Floating Point Format
7 | 2 | Net Flow Rate | 401108 | Floating Point Format
8 | 2 | Gross Accumulator | 401109 | Long Integer Format
9 | 2 | Gross Accumulator | 401110 | Long Integer Format
10 | 2 | Gross Standard Accumulator | 401111 | Long Integer Format
11 | 2 | Gross Standard Accumulator | 401112 | Long Integer Format
12 | 2 | Mass Accumulator | 401113 | Long Integer Format
13 | 2 | Mass Accumulator | 401114 | Long Integer Format
14 | 2 | Reserved | 401115
15 | 2 | Reserved | 401116
16 | 2 | Reserved | 401117
17 | 2 | Reserved | 401118
18 | 2 | Reserved | 401119
19 | 2 | Reserved | 401120
20 | 2 | Reserved | 401121
21 | 2 | Reserved | 401122
22 | 2 | Reserved | 401123
23 | 2 | Reserved | 401124
24 | 2 | Reserved | 401125
25 | 2 | Reserved | 401126
26 | 2 | Reserved | 401127
27 | 2 | Reserved | 401128
28 | 2 | Reserved | 401129
29 | 2 | Reserved | 401130
30 | 2 | Reserved | 401131
31 | 2 | Reserved | 401132
32 | 2 | Reserved | 401133
33 | 2 | Reserved | 401134
34 | 2 | Reserved | 401135
35 | 2 | Reserved | 401136
36 | 2 | Reserved | 401137
37 | 2 | Reserved | 401138
Meter 3 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Scan Count: process input | 401301
1 | 3 | Scan Count: calculation | 401302
2 | 3 | Meter in Alarm | 401303 | 0=no alarm
3 | 3 | Reserved | 401304
4 | 3 | Net Accumulator | 401305 | Long Integer Format
5 | 3 | Net Accumulator | 401306 | Long Integer Format
6 | 3 | Net Flow Rate | 401307 | Floating Point Format
7 | 3 | Net Flow Rate | 401308 | Floating Point Format
8 | 3 | Gross Accumulator | 401309 | Long Integer Format
9 | 3 | Gross Accumulator | 401310 | Long Integer Format
10 | 3 | Gross Standard Accumulator | 401311 | Long Integer Format
11 | 3 | Gross Standard Accumulator | 401312 | Long Integer Format
12 | 3 | Mass Accumulator | 401313 | Long Integer Format
13 | 3 | Mass Accumulator | 401314 | Long Integer Format
14 | 3 | Reserved | 401315
15 | 3 | Reserved | 401316
16 | 3 | Reserved | 401317
17 | 3 | Reserved | 401318
18 | 3 | Reserved | 401319
19 | 3 | Reserved | 401320
20 | 3 | Reserved | 401321
21 | 3 | Reserved | 401322
22 | 3 | Reserved | 401323
23 | 3 | Reserved | 401324
24 | 3 | Reserved | 401325
25 | 3 | Reserved | 401326
26 | 3 | Reserved | 401327
27 | 3 | Reserved | 401328
28 | 3 | Reserved | 401329
29 | 3 | Reserved | 401330
30 | 3 | Reserved | 401331
31 | 3 | Reserved | 401332
32 | 3 | Reserved | 401333
33 | 3 | Reserved | 401334
34 | 3 | Reserved | 401335
35 | 3 | Reserved | 401336
36 | 3 | Reserved | 401337
37 | 3 | Reserved | 401338
Meter 4 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Scan Count: process input | 401501
1 | 4 | Scan Count: calculation | 401502
2 | 4 | Meter in Alarm | 401503 | 0=no alarm
3 | 4 | Reserved | 401504
4 | 4 | Net Accumulator | 401505 | Long Integer Format
5 | 4 | Net Accumulator | 401506 | Long Integer Format
6 | 4 | Net Flow Rate | 401507 | Floating Point Format
7 | 4 | Net Flow Rate | 401508 | Floating Point Format
8 | 4 | Gross Accumulator | 401509 | Long Integer Format
9 | 4 | Gross Accumulator | 401510 | Long Integer Format
10 | 4 | Gross Standard Accumulator | 401511 | Long Integer Format
11 | 4 | Gross Standard Accumulator | 401512 | Long Integer Format
12 | 4 | Mass Accumulator | 401513 | Long Integer Format
13 | 4 | Mass Accumulator | 401514 | Long Integer Format
14 | 4 | Reserved | 401515
15 | 4 | Reserved | 401516
16 | 4 | Reserved | 401517
17 | 4 | Reserved | 401518
18 | 4 | Reserved | 401519
19 | 4 | Reserved | 401520
20 | 4 | Reserved | 401521
21 | 4 | Reserved | 401522
22 | 4 | Reserved | 401523
23 | 4 | Reserved | 401524
24 | 4 | Reserved | 401525
25 | 4 | Reserved | 401526
26 | 4 | Reserved | 401527
27 | 4 | Reserved | 401528
28 | 4 | Reserved | 401529
29 | 4 | Reserved | 401530
30 | 4 | Reserved | 401531
31 | 4 | Reserved | 401532
32 | 4 | Reserved | 401533
33 | 4 | Reserved | 401534
34 | 4 | Reserved | 401535
35 | 4 | Reserved | 401536
36 | 4 | Reserved | 401537
37 | 4 | Reserved | 401538
Meter 5 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Scan Count: process input | 401701
1 | 5 | Scan Count: calculation | 401702
2 | 5 | Meter in Alarm | 401703 | 0=no alarm
3 | 5 | Reserved | 401704
4 | 5 | Net Accumulator | 401705 | Long Integer Format
5 | 5 | Net Accumulator | 401706 | Long Integer Format
6 | 5 | Net Flow Rate | 401707 | Floating Point Format
7 | 5 | Net Flow Rate | 401708 | Floating Point Format
8 | 5 | Gross Accumulator | 401709 | Long Integer Format
9 | 5 | Gross Accumulator | 401710 | Long Integer Format
10 | 5 | Gross Standard Accumulator | 401711 | Long Integer Format
11 | 5 | Gross Standard Accumulator | 401712 | Long Integer Format
12 | 5 | Mass Accumulator | 401713 | Long Integer Format
13 | 5 | Mass Accumulator | 401714 | Long Integer Format
14 | 5 | Reserved | 401715
15 | 5 | Reserved | 401716
16 | 5 | Reserved | 401717
17 | 5 | Reserved | 401718
18 | 5 | Reserved | 401719
19 | 5 | Reserved | 401720
20 | 5 | Reserved | 401721
21 | 5 | Reserved | 401722
22 | 5 | Reserved | 401723
23 | 5 | Reserved | 401724
24 | 5 | Reserved | 401725
25 | 5 | Reserved | 401726
26 | 5 | Reserved | 401727
27 | 5 | Reserved | 401728
28 | 5 | Reserved | 401729
29 | 5 | Reserved | 401730
30 | 5 | Reserved | 401731
31 | 5 | Reserved | 401732
32 | 5 | Reserved | 401733
33 | 5 | Reserved | 401734
34 | 5 | Reserved | 401735
35 | 5 | Reserved | 401736
36 | 5 | Reserved | 401737
37 | 5 | Reserved | 401738
Meter 6 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Scan Count: process input | 401901
1 | 6 | Scan Count: calculation | 401902
2 | 6 | Meter in Alarm | 401903 | 0=no alarm
3 | 6 | Reserved | 401904
4 | 6 | Net Accumulator | 401905 | Long Integer Format
5 | 6 | Net Accumulator | 401906 | Long Integer Format
6 | 6 | Net Flow Rate | 401907 | Floating Point Format
7 | 6 | Net Flow Rate | 401908 | Floating Point Format
8 | 6 | Gross Accumulator | 401909 | Long Integer Format
9 | 6 | Gross Accumulator | 401910 | Long Integer Format
10 | 6 | Gross Standard Accumulator | 401911 | Long Integer Format
11 | 6 | Gross Standard Accumulator | 401912 | Long Integer Format
12 | 6 | Mass Accumulator | 401913 | Long Integer Format
13 | 6 | Mass Accumulator | 401914 | Long Integer Format
14 | 6 | Reserved | 401915
15 | 6 | Reserved | 401916
16 | 6 | Reserved | 401917
17 | 6 | Reserved | 401918
18 | 6 | Reserved | 401919
19 | 6 | Reserved | 401920
20 | 6 | Reserved | 401921
21 | 6 | Reserved | 401922
22 | 6 | Reserved | 401923
23 | 6 | Reserved | 401924
24 | 6 | Reserved | 401925
25 | 6 | Reserved | 401926
26 | 6 | Reserved | 401927
27 | 6 | Reserved | 401928
28 | 6 | Reserved | 401929
29 | 6 | Reserved | 401930
30 | 6 | Reserved | 401931
31 | 6 | Reserved | 401932
32 | 6 | Reserved | 401933
33 | 6 | Reserved | 401934
34 | 6 | Reserved | 401935
35 | 6 | Reserved | 401936
36 | 6 | Reserved | 401937
37 | 6 | Reserved | 401938
Meter 7 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Scan Count: process input | 402101
1 | 7 | Scan Count: calculation | 402102
2 | 7 | Meter in Alarm | 402103 | 0=no alarm
3 | 7 | Reserved | 402104
4 | 7 | Net Accumulator | 402105 | Long Integer Format
5 | 7 | Net Accumulator | 402106 | Long Integer Format
6 | 7 | Net Flow Rate | 402107 | Floating Point Format
7 | 7 | Net Flow Rate | 402108 | Floating Point Format
8 | 7 | Gross Accumulator | 402109 | Long Integer Format
9 | 7 | Gross Accumulator | 402110 | Long Integer Format
10 | 7 | Gross Standard Accumulator | 402111 | Long Integer Format
11 | 7 | Gross Standard Accumulator | 402112 | Long Integer Format
12 | 7 | Mass Accumulator | 402113 | Long Integer Format
13 | 7 | Mass Accumulator | 402114 | Long Integer Format
14 | 7 | Reserved | 402115
15 | 7 | Reserved | 402116
16 | 7 | Reserved | 402117
17 | 7 | Reserved | 402118
18 | 7 | Reserved | 402119
19 | 7 | Reserved | 402120
20 | 7 | Reserved | 402121
21 | 7 | Reserved | 402122
22 | 7 | Reserved | 402123
23 | 7 | Reserved | 402124
24 | 7 | Reserved | 402125
25 | 7 | Reserved | 402126
26 | 7 | Reserved | 402127
27 | 7 | Reserved | 402128
28 | 7 | Reserved | 402129
29 | 7 | Reserved | 402130
30 | 7 | Reserved | 402131
31 | 7 | Reserved | 402132
32 | 7 | Reserved | 402133
33 | 7 | Reserved | 402134
34 | 7 | Reserved | 402135
35 | 7 | Reserved | 402136
36 | 7 | Reserved | 402137
37 | 7 | Reserved | 402138
Meter 8 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Scan Count: process input | 402301
1 | 8 | Scan Count: calculation | 402302
2 | 8 | Meter in Alarm | 402303 | 0=no alarm
3 | 8 | Reserved | 402304
4 | 8 | Net Accumulator | 402305 | Long Integer Format
5 | 8 | Net Accumulator | 402306 | Long Integer Format
6 | 8 | Net Flow Rate | 402307 | Floating Point Format
7 | 8 | Net Flow Rate | 402308 | Floating Point Format
8 | 8 | Gross Accumulator | 402309 | Long Integer Format
9 | 8 | Gross Accumulator | 402310 | Long Integer Format
10 | 8 | Gross Standard Accumulator | 402311 | Long Integer Format
11 | 8 | Gross Standard Accumulator | 402312 | Long Integer Format
12 | 8 | Mass Accumulator | 402313 | Long Integer Format
13 | 8 | Mass Accumulator | 402314 | Long Integer Format
14 | 8 | Reserved | 402315
15 | 8 | Reserved | 402316
16 | 8 | Reserved | 402317
17 | 8 | Reserved | 402318
18 | 8 | Reserved | 402319
19 | 8 | Reserved | 402320
20 | 8 | Reserved | 402321
21 | 8 | Reserved | 402322
22 | 8 | Reserved | 402323
23 | 8 | Reserved | 402324
24 | 8 | Reserved | 402325
25 | 8 | Reserved | 402326
26 | 8 | Reserved | 402327
27 | 8 | Reserved | 402328
28 | 8 | Reserved | 402329
29 | 8 | Reserved | 402330
30 | 8 | Reserved | 402331
31 | 8 | Reserved | 402332
32 | 8 | Reserved | 402333
33 | 8 | Reserved | 402334
34 | 8 | Reserved | 402335
35 | 8 | Reserved | 402336
36 | 8 | Reserved | 402337
37 | 8 | Reserved | 402338
Meter 9 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Scan Count: process input | 402501
1 | 9 | Scan Count: calculation | 402502
2 | 9 | Meter in Alarm | 402503 | 0=no alarm
3 | 9 | Reserved | 402504
4 | 9 | Net Accumulator | 402505 | Long Integer Format
5 | 9 | Net Accumulator | 402506 | Long Integer Format
6 | 9 | Net Flow Rate | 402507 | Floating Point Format
7 | 9 | Net Flow Rate | 402508 | Floating Point Format
8 | 9 | Gross Accumulator | 402509 | Long Integer Format
9 | 9 | Gross Accumulator | 402510 | Long Integer Format
10 | 9 | Gross Standard Accumulator | 402511 | Long Integer Format
11 | 9 | Gross Standard Accumulator | 402512 | Long Integer Format
12 | 9 | Mass Accumulator | 402513 | Long Integer Format
13 | 9 | Mass Accumulator | 402514 | Long Integer Format
14 | 9 | Reserved | 402515
15 | 9 | Reserved | 402516
16 | 9 | Reserved | 402517
17 | 9 | Reserved | 402518
18 | 9 | Reserved | 402519
19 | 9 | Reserved | 402520
20 | 9 | Reserved | 402521
21 | 9 | Reserved | 402522
22 | 9 | Reserved | 402523
23 | 9 | Reserved | 402524
24 | 9 | Reserved | 402525
25 | 9 | Reserved | 402526
26 | 9 | Reserved | 402527
27 | 9 | Reserved | 402528
28 | 9 | Reserved | 402529
29 | 9 | Reserved | 402530
30 | 9 | Reserved | 402531
31 | 9 | Reserved | 402532
32 | 9 | Reserved | 402533
33 | 9 | Reserved | 402534
34 | 9 | Reserved | 402535
35 | 9 | Reserved | 402536
36 | 9 | Reserved | 402537
37 | 9 | Reserved | 402538
Meter 10 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Scan Count: process input | 402701
1 | 10 | Scan Count: calculation | 402702
2 | 10 | Meter in Alarm | 402703 | 0=no alarm
3 | 10 | Reserved | 402704
4 | 10 | Net Accumulator | 402705 | Long Integer Format
5 | 10 | Net Accumulator | 402706 | Long Integer Format
6 | 10 | Net Flow Rate | 402707 | Floating Point Format
7 | 10 | Net Flow Rate | 402708 | Floating Point Format
8 | 10 | Gross Accumulator | 402709 | Long Integer Format
9 | 10 | Gross Accumulator | 402710 | Long Integer Format
10 | 10 | Gross Standard Accumulator | 402711 | Long Integer Format
11 | 10 | Gross Standard Accumulator | 402712 | Long Integer Format
12 | 10 | Mass Accumulator | 402713 | Long Integer Format
13 | 10 | Mass Accumulator | 402714 | Long Integer Format
14 | 10 | Reserved | 402715
15 | 10 | Reserved | 402716
16 | 10 | Reserved | 402717
17 | 10 | Reserved | 402718
18 | 10 | Reserved | 402719
19 | 10 | Reserved | 402720
20 | 10 | Reserved | 402721
21 | 10 | Reserved | 402722
22 | 10 | Reserved | 402723
23 | 10 | Reserved | 402724
24 | 10 | Reserved | 402725
25 | 10 | Reserved | 402726
26 | 10 | Reserved | 402727
27 | 10 | Reserved | 402728
28 | 10 | Reserved | 402729
29 | 10 | Reserved | 402730
30 | 10 | Reserved | 402731
31 | 10 | Reserved | 402732
32 | 10 | Reserved | 402733
33 | 10 | Reserved | 402734
34 | 10 | Reserved | 402735
35 | 10 | Reserved | 402736
36 | 10 | Reserved | 402737
37 | 10 | Reserved | 402738
Meter 11 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Scan Count: process input | 402901
1 | 11 | Scan Count: calculation | 402902
2 | 11 | Meter in Alarm | 402903 | 0=no alarm
3 | 11 | Reserved | 402904
4 | 11 | Net Accumulator | 402905 | Long Integer Format
5 | 11 | Net Accumulator | 402906 | Long Integer Format
6 | 11 | Net Flow Rate | 402907 | Floating Point Format
7 | 11 | Net Flow Rate | 402908 | Floating Point Format
8 | 11 | Gross Accumulator | 402909 | Long Integer Format
9 | 11 | Gross Accumulator | 402910 | Long Integer Format
10 | 11 | Gross Standard Accumulator | 402911 | Long Integer Format
11 | 11 | Gross Standard Accumulator | 402912 | Long Integer Format
12 | 11 | Mass Accumulator | 402913 | Long Integer Format
13 | 11 | Mass Accumulator | 402914 | Long Integer Format
14 | 11 | Reserved | 402915
15 | 11 | Reserved | 402916
16 | 11 | Reserved | 402917
17 | 11 | Reserved | 402918
18 | 11 | Reserved | 402919
19 | 11 | Reserved | 402920
20 | 11 | Reserved | 402921
21 | 11 | Reserved | 402922
22 | 11 | Reserved | 402923
23 | 11 | Reserved | 402924
24 | 11 | Reserved | 402925
25 | 11 | Reserved | 402926
26 | 11 | Reserved | 402927
27 | 11 | Reserved | 402928
28 | 11 | Reserved | 402929
29 | 11 | Reserved | 402930
30 | 11 | Reserved | 402931
31 | 11 | Reserved | 402932
32 | 11 | Reserved | 402933
33 | 11 | Reserved | 402934
34 | 11 | Reserved | 402935
35 | 11 | Reserved | 402936
36 | 11 | Reserved | 402937
37 | 11 | Reserved | 402938
Meter 12 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Scan Count: process input | 403101
1 | 12 | Scan Count: calculation | 403102
2 | 12 | Meter in Alarm | 403103 | 0=no alarm
3 | 12 | Reserved | 403104
4 | 12 | Net Accumulator | 403105 | Long Integer Format
5 | 12 | Net Accumulator | 403106 | Long Integer Format
6 | 12 | Net Flow Rate | 403107 | Floating Point Format
7 | 12 | Net Flow Rate | 403108 | Floating Point Format
8 | 12 | Gross Accumulator | 403109 | Long Integer Format
9 | 12 | Gross Accumulator | 403110 | Long Integer Format
10 | 12 | Gross Standard Accumulator | 403111 | Long Integer Format
11 | 12 | Gross Standard Accumulator | 403112 | Long Integer Format
12 | 12 | Mass Accumulator | 403113 | Long Integer Format
13 | 12 | Mass Accumulator | 403114 | Long Integer Format
14 | 12 | Reserved | 403115
15 | 12 | Reserved | 403116
16 | 12 | Reserved | 403117
17 | 12 | Reserved | 403118
18 | 12 | Reserved | 403119
19 | 12 | Reserved | 403120
20 | 12 | Reserved | 403121
21 | 12 | Reserved | 403122
22 | 12 | Reserved | 403123
23 | 12 | Reserved | 403124
24 | 12 | Reserved | 403125
25 | 12 | Reserved | 403126
26 | 12 | Reserved | 403127
27 | 12 | Reserved | 403128
28 | 12 | Reserved | 403129
29 | 12 | Reserved | 403130
30 | 12 | Reserved | 403131
31 | 12 | Reserved | 403132
32 | 12 | Reserved | 403133
33 | 12 | Reserved | 403134
34 | 12 | Reserved | 403135
35 | 12 | Reserved | 403136
36 | 12 | Reserved | 403137
37 | 12 | Reserved | 403138
Meter 13 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Scan Count: process input | 403301
1 | 13 | Scan Count: calculation | 403302
2 | 13 | Meter in Alarm | 403303 | 0=no alarm
3 | 13 | Reserved | 403304
4 | 13 | Net Accumulator | 403305 | Long Integer Format
5 | 13 | Net Accumulator | 403306 | Long Integer Format
6 | 13 | Net Flow Rate | 403307 | Floating Point Format
7 | 13 | Net Flow Rate | 403308 | Floating Point Format
8 | 13 | Gross Accumulator | 403309 | Long Integer Format
9 | 13 | Gross Accumulator | 403310 | Long Integer Format
10 | 13 | Gross Standard Accumulator | 403311 | Long Integer Format
11 | 13 | Gross Standard Accumulator | 403312 | Long Integer Format
12 | 13 | Mass Accumulator | 403313 | Long Integer Format
13 | 13 | Mass Accumulator | 403314 | Long Integer Format
14 | 13 | Reserved | 403315
15 | 13 | Reserved | 403316
16 | 13 | Reserved | 403317
17 | 13 | Reserved | 403318
18 | 13 | Reserved | 403319
19 | 13 | Reserved | 403320
20 | 13 | Reserved | 403321
21 | 13 | Reserved | 403322
22 | 13 | Reserved | 403323
23 | 13 | Reserved | 403324
24 | 13 | Reserved | 403325
25 | 13 | Reserved | 403326
26 | 13 | Reserved | 403327
27 | 13 | Reserved | 403328
28 | 13 | Reserved | 403329
29 | 13 | Reserved | 403330
30 | 13 | Reserved | 403331
31 | 13 | Reserved | 403332
32 | 13 | Reserved | 403333
33 | 13 | Reserved | 403334
34 | 13 | Reserved | 403335
35 | 13 | Reserved | 403336
36 | 13 | Reserved | 403337
37 | 13 | Reserved | 403338
Meter 14 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Scan Count: process input | 403501
1 | 14 | Scan Count: calculation | 403502
2 | 14 | Meter in Alarm | 403503 | 0=no alarm
3 | 14 | Reserved | 403504
4 | 14 | Net Accumulator | 403505 | Long Integer Format
5 | 14 | Net Accumulator | 403506 | Long Integer Format
6 | 14 | Net Flow Rate | 403507 | Floating Point Format
7 | 14 | Net Flow Rate | 403508 | Floating Point Format
8 | 14 | Gross Accumulator | 403509 | Long Integer Format
9 | 14 | Gross Accumulator | 403510 | Long Integer Format
10 | 14 | Gross Standard Accumulator | 403511 | Long Integer Format
11 | 14 | Gross Standard Accumulator | 403512 | Long Integer Format
12 | 14 | Mass Accumulator | 403513 | Long Integer Format
13 | 14 | Mass Accumulator | 403514 | Long Integer Format
14 | 14 | Reserved | 403515
15 | 14 | Reserved | 403516
16 | 14 | Reserved | 403517
17 | 14 | Reserved | 403518
18 | 14 | Reserved | 403519
19 | 14 | Reserved | 403520
20 | 14 | Reserved | 403521
21 | 14 | Reserved | 403522
22 | 14 | Reserved | 403523
23 | 14 | Reserved | 403524
24 | 14 | Reserved | 403525
25 | 14 | Reserved | 403526
26 | 14 | Reserved | 403527
27 | 14 | Reserved | 403528
28 | 14 | Reserved | 403529
29 | 14 | Reserved | 403530
30 | 14 | Reserved | 403531
31 | 14 | Reserved | 403532
32 | 14 | Reserved | 403533
33 | 14 | Reserved | 403534
34 | 14 | Reserved | 403535
35 | 14 | Reserved | 403536
36 | 14 | Reserved | 403537
37 | 14 | Reserved | 403538
Meter 15 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Scan Count: process input | 403701
1 | 15 | Scan Count: calculation | 403702
2 | 15 | Meter in Alarm | 403703 | 0=no alarm
3 | 15 | Reserved | 403704
4 | 15 | Net Accumulator | 403705 | Long Integer Format
5 | 15 | Net Accumulator | 403706 | Long Integer Format
6 | 15 | Net Flow Rate | 403707 | Floating Point Format
7 | 15 | Net Flow Rate | 403708 | Floating Point Format
8 | 15 | Gross Accumulator | 403709 | Long Integer Format
9 | 15 | Gross Accumulator | 403710 | Long Integer Format
10 | 15 | Gross Standard Accumulator | 403711 | Long Integer Format
11 | 15 | Gross Standard Accumulator | 403712 | Long Integer Format
12 | 15 | Mass Accumulator | 403713 | Long Integer Format
13 | 15 | Mass Accumulator | 403714 | Long Integer Format
14 | 15 | Reserved | 403715
15 | 15 | Reserved | 403716
16 | 15 | Reserved | 403717
17 | 15 | Reserved | 403718
18 | 15 | Reserved | 403719
19 | 15 | Reserved | 403720
20 | 15 | Reserved | 403721
21 | 15 | Reserved | 403722
22 | 15 | Reserved | 403723
23 | 15 | Reserved | 403724
24 | 15 | Reserved | 403725
25 | 15 | Reserved | 403726
26 | 15 | Reserved | 403727
27 | 15 | Reserved | 403728
28 | 15 | Reserved | 403729
29 | 15 | Reserved | 403730
30 | 15 | Reserved | 403731
31 | 15 | Reserved | 403732
32 | 15 | Reserved | 403733
33 | 15 | Reserved | 403734
34 | 15 | Reserved | 403735
35 | 15 | Reserved | 403736
36 | 15 | Reserved | 403737
37 | 15 | Reserved | 403738
Meter 16 Results Orifice & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Scan Count: process input | 403901
1 | 16 | Scan Count: calculation | 403902
2 | 16 | Meter in Alarm | 403903 | 0=no alarm
3 | 16 | Reserved | 403904
4 | 16 | Net Accumulator | 403905 | Long Integer Format
5 | 16 | Net Accumulator | 403906 | Long Integer Format
6 | 16 | Net Flow Rate | 403907 | Floating Point Format
7 | 16 | Net Flow Rate | 403908 | Floating Point Format
8 | 16 | Gross Accumulator | 403909 | Long Integer Format
9 | 16 | Gross Accumulator | 403910 | Long Integer Format
10 | 16 | Gross Standard Accumulator | 403911 | Long Integer Format
11 | 16 | Gross Standard Accumulator | 403912 | Long Integer Format
12 | 16 | Mass Accumulator | 403913 | Long Integer Format
13 | 16 | Mass Accumulator | 403914 | Long Integer Format
14 | 16 | Reserved | 403915
15 | 16 | Reserved | 403916
16 | 16 | Reserved | 403917
17 | 16 | Reserved | 403918
18 | 16 | Reserved | 403919
19 | 16 | Reserved | 403920
20 | 16 | Reserved | 403921
21 | 16 | Reserved | 403922
22 | 16 | Reserved | 403923
23 | 16 | Reserved | 403924
24 | 16 | Reserved | 403925
25 | 16 | Reserved | 403926
26 | 16 | Reserved | 403927
27 | 16 | Reserved | 403928
28 | 16 | Reserved | 403929
29 | 16 | Reserved | 403930
30 | 16 | Reserved | 403931
31 | 16 | Reserved | 403932
32 | 16 | Reserved | 403933
33 | 16 | Reserved | 403934
34 | 16 | Reserved | 403935
35 | 16 | Reserved | 403936
36 | 16 | Reserved | 403937
37 | 16 | Reserved | 403938

## Meter Variables - Pulse & Liq
Meter 1 Variables Pulse & Liq
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Meter Disable | 400801
1 | 1 | Water % | 400802 | Scaled Integer Format
2 | 1 | Temperature | 400803 | Floating Point Format
3 | 1 | Temperature | 400804 | Floating Point Format
4 | 1 | Pressure | 400805 | Floating Point Format
5 | 1 | Pressure | 400806 | Floating Point Format
6 | 1 | Meter Pulses | 400807 | Double Integer Format
7 | 1 | Meter Pulses | 400808 | Double Integer Format
8 | 1 | Density | 400809 | Floating Point Format
9 | 1 | Density | 400810 | Floating Point Format
10 | 1 | Pulse Frequency | 400811 | Floating Point Format
11 | 1 | Pulse Frequency | 400812 | Floating Point Format
12 | 1 | Molar Analysis - C1 | 400813 | Scaled Integer Format (10000 = 100%)
13 | 1 | Molar Analysis - N2 | 400814 | Scaled Integer Format (10000 = 100%)
14 | 1 | Molar Analysis - CO2 | 400815 | Scaled Integer Format (10000 = 100%)
15 | 1 | Molar Analysis - C2 | 400816 | Scaled Integer Format (10000 = 100%)
16 | 1 | Molar Analysis - C3 | 400817 | Scaled Integer Format (10000 = 100%)
17 | 1 | Molar Analysis - H2O | 400818 | Scaled Integer Format (10000 = 100%)
18 | 1 | Molar Analysis - H2S | 400819 | Scaled Integer Format (10000 = 100%)
19 | 1 | Molar Analysis - H2 | 400820 | Scaled Integer Format (10000 = 100%)
20 | 1 | Molar Analysis - CO | 400821 | Scaled Integer Format (10000 = 100%)
21 | 1 | Molar Analysis - O2 | 400822 | Scaled Integer Format (10000 = 100%)
22 | 1 | Molar Analysis - iC4 | 400823 | Scaled Integer Format (10000 = 100%)
23 | 1 | Molar Analysis - C4 | 400824 | Scaled Integer Format (10000 = 100%)
24 | 1 | Molar Analysis - iC5 | 400825 | Scaled Integer Format (10000 = 100%)
25 | 1 | Molar Analysis - C5 | 400826 | Scaled Integer Format (10000 = 100%)
26 | 1 | Molar Analysis - C6 | 400827 | Scaled Integer Format (10000 = 100%)
27 | 1 | Molar Analysis - C7 | 400828 | Scaled Integer Format (10000 = 100%)
28 | 1 | Molar Analysis - C8 | 400829 | Scaled Integer Format (10000 = 100%)
29 | 1 | Molar Analysis - C9 | 400830 | Scaled Integer Format (10000 = 100%)
30 | 1 | Molar Analysis - C10 | 400831 | Scaled Integer Format (10000 = 100%)
31 | 1 | Molar Analysis - He | 400832 | Scaled Integer Format (10000 = 100%)
32 | 1 | Molar Analysis - Ar | 400833 | Scaled Integer Format (10000 = 100%)
33 | 1 | Molar Analysis - C5 (neo-p) | 400834 | Scaled Integer Format (10000 = 100%)
34 | 1 | Molar Analysis - Ux | 400835 | Scaled Integer Format (10000 = 100%)
35 | 1 | Molar Analysis - Uy | 400836 | Scaled Integer Format (10000 = 100%)
36 | 1 | Meter Signals - Reserved | 400837
37 | 1 | Meter Signals - Reserved | 400838
38 | 1 | Meter Signals - Reserved | 400839
39 | 1 | Meter Signals - Reserved | 400840
40 | 1 | Meter Signals - Reset Acc 1 | 400841
41 | 1 | Meter Signals - Reset Acc 2 | 400842
42 | 1 | Meter Signals - Reset Acc 3 | 400843
43 | 1 | Meter Signals - Reset Acc 4 | 400844
44 | 1 | Write Daily Archive | 400845
45 | 1 | Write Hourly Archive | 400846
46 | 1 | Meter Signals - Reserved | 400847
47 | 1 | Meter Signals - Reserved | 400848
48 | 1 | Meter Signals - Reserved | 400849
49 | 1 | Meter Signals - Reserved | 400850
50 | 1 | Meter Signals - Reserved | 400851
51 | 1 | Meter Signals - Reserved | 400852
52 | 1 | Analysis is Present | 400853
53 | 1 | Meter Archive Record Fetch | 400854 | (=0 signal not present)
54 | 1 | Meter Archive Record Age | 400855 | (=0 current)
55 | 1 | Meter Archive File Select | 400856 | (=0 daily, 1=hourly)
Meter 2 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Meter Disable | 401001
1 | 2 | Water % | 401002 | Scaled Integer Format
2 | 2 | Temperature | 401003 | Floating Point Format
3 | 2 | Temperature | 401004 | Floating Point Format
4 | 2 | Pressure | 401005 | Floating Point Format
5 | 2 | Pressure | 401006 | Floating Point Format
6 | 2 | Pulse Count | 401007 | Long Integer
7 | 2 | Pulse Count | 401008 | Long Integer
8 | 2 | Density | 401009 | Floating Point Format
9 | 2 | Density | 401010 | Floating Point Format
10 | 2 | Pulse Frequency | 401011 | Floating Point Format
11 | 2 | Pulse Frequency | 401012 | Floating Point Format
12 | 2 | Molar Analysis - C1 | 401013 | Scaled Integer Format (10000 = 100%)
13 | 2 | Molar Analysis - N2 | 401014 | Scaled Integer Format (10000 = 100%)
14 | 2 | Molar Analysis - CO2 | 401015 | Scaled Integer Format (10000 = 100%)
15 | 2 | Molar Analysis - C2 | 401016 | Scaled Integer Format (10000 = 100%)
16 | 2 | Molar Analysis - C3 | 401017 | Scaled Integer Format (10000 = 100%)
17 | 2 | Molar Analysis - H2O | 401018 | Scaled Integer Format (10000 = 100%)
18 | 2 | Molar Analysis - H2S | 401019 | Scaled Integer Format (10000 = 100%)
19 | 2 | Molar Analysis - H2 | 401020 | Scaled Integer Format (10000 = 100%)
20 | 2 | Molar Analysis - CO | 401021 | Scaled Integer Format (10000 = 100%)
21 | 2 | Molar Analysis - O2 | 401022 | Scaled Integer Format (10000 = 100%)
22 | 2 | Molar Analysis - iC4 | 401023 | Scaled Integer Format (10000 = 100%)
23 | 2 | Molar Analysis - C4 | 401024 | Scaled Integer Format (10000 = 100%)
24 | 2 | Molar Analysis - iC5 | 401025 | Scaled Integer Format (10000 = 100%)
25 | 2 | Molar Analysis - C5 | 401026 | Scaled Integer Format (10000 = 100%)
26 | 2 | Molar Analysis - C6 | 401027 | Scaled Integer Format (10000 = 100%)
27 | 2 | Molar Analysis - C7 | 401028 | Scaled Integer Format (10000 = 100%)
28 | 2 | Molar Analysis - C8 | 401029 | Scaled Integer Format (10000 = 100%)
29 | 2 | Molar Analysis - C9 | 401030 | Scaled Integer Format (10000 = 100%)
30 | 2 | Molar Analysis - C10 | 401031 | Scaled Integer Format (10000 = 100%)
31 | 2 | Molar Analysis - He | 401032 | Scaled Integer Format (10000 = 100%)
32 | 2 | Molar Analysis - Ar | 401033 | Scaled Integer Format (10000 = 100%)
33 | 2 | Molar Analysis - C5 (neo-p) | 401034 | Scaled Integer Format (10000 = 100%)
34 | 2 | Molar Analysis - Ux | 401035 | Scaled Integer Format (10000 = 100%)
35 | 2 | Molar Analysis - Uy | 401036 | Scaled Integer Format (10000 = 100%)
36 | 2 | Meter Signals - Reserved | 401037
37 | 2 | Meter Signals - Reserved | 401038
38 | 2 | Meter Signals - Reserved | 401039
39 | 2 | Meter Signals - Reserved | 401040
40 | 2 | Meter Signals - Reset Acc 1 | 401041
41 | 2 | Meter Signals - Reset Acc 2 | 401042
42 | 2 | Meter Signals - Reset Acc 3 | 401043
43 | 2 | Meter Signals - Reset Acc 4 | 401044
44 | 2 | Write Daily Archive | 401045
45 | 2 | Write Hourly Archive | 401046
46 | 2 | Meter Signals - Reserved | 401047
47 | 2 | Meter Signals - Reserved | 401048
48 | 2 | Meter Signals - Reserved | 401049
49 | 2 | Meter Signals - Reserved | 401050
50 | 2 | Meter Signals - Reserved | 401051
51 | 2 | Meter Signals - Reserved | 401052
52 | 2 | Analysis is Present | 401053
53 | 2 | Meter Archive Record Fetch | 401054 | (=0 signal not present)
54 | 2 | Meter Archive Record Age | 401055 | (=0 current)
55 | 2 | Meter Archive File Select | 401056 | (=0 daily, 1=hourly)
Meter 3 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Meter Disable | 401201
1 | 3 | Water % | 401202 | Scaled Integer Format
2 | 3 | Temperature | 401203 | Floating Point Format
3 | 3 | Temperature | 401204 | Floating Point Format
4 | 3 | Pressure | 401205 | Floating Point Format
5 | 3 | Pressure | 401206 | Floating Point Format
6 | 3 | Differential Pressure | 401207 | Long Integer Format
7 | 3 | Differential Pressure | 401208 | Long Integer Format
8 | 3 | Density | 401209 | Floating Point Format
9 | 3 | Density | 401210 | Floating Point Format
10 | 3 | Pulse Frequency | 401211 | Floating Point Format
11 | 3 | Pulse Frequency | 401212 | Floating Point Format
12 | 3 | Molar Analysis - C1 | 401213 | Scaled Integer Format (10000 = 100%)
13 | 3 | Molar Analysis - N2 | 401214 | Scaled Integer Format (10000 = 100%)
14 | 3 | Molar Analysis - CO2 | 401215 | Scaled Integer Format (10000 = 100%)
15 | 3 | Molar Analysis - C2 | 401216 | Scaled Integer Format (10000 = 100%)
16 | 3 | Molar Analysis - C3 | 401217 | Scaled Integer Format (10000 = 100%)
17 | 3 | Molar Analysis - H2O | 401218 | Scaled Integer Format (10000 = 100%)
18 | 3 | Molar Analysis - H2S | 401219 | Scaled Integer Format (10000 = 100%)
19 | 3 | Molar Analysis - H2 | 401220 | Scaled Integer Format (10000 = 100%)
20 | 3 | Molar Analysis - CO | 401221 | Scaled Integer Format (10000 = 100%)
21 | 3 | Molar Analysis - O2 | 401222 | Scaled Integer Format (10000 = 100%)
22 | 3 | Molar Analysis - iC4 | 401223 | Scaled Integer Format (10000 = 100%)
23 | 3 | Molar Analysis - C4 | 401224 | Scaled Integer Format (10000 = 100%)
24 | 3 | Molar Analysis - iC5 | 401225 | Scaled Integer Format (10000 = 100%)
25 | 3 | Molar Analysis - C5 | 401226 | Scaled Integer Format (10000 = 100%)
26 | 3 | Molar Analysis - C6 | 401227 | Scaled Integer Format (10000 = 100%)
27 | 3 | Molar Analysis - C7 | 401228 | Scaled Integer Format (10000 = 100%)
28 | 3 | Molar Analysis - C8 | 401229 | Scaled Integer Format (10000 = 100%)
29 | 3 | Molar Analysis - C9 | 401230 | Scaled Integer Format (10000 = 100%)
30 | 3 | Molar Analysis - C10 | 401231 | Scaled Integer Format (10000 = 100%)
31 | 3 | Molar Analysis - He | 401232 | Scaled Integer Format (10000 = 100%)
32 | 3 | Molar Analysis - Ar | 401233 | Scaled Integer Format (10000 = 100%)
33 | 3 | Molar Analysis - C5 (neo-p) | 401234 | Scaled Integer Format (10000 = 100%)
34 | 3 | Molar Analysis - Ux | 401235 | Scaled Integer Format (10000 = 100%)
35 | 3 | Molar Analysis - Uy | 401236 | Scaled Integer Format (10000 = 100%)
36 | 3 | Meter Signals - Reserved | 401237
37 | 3 | Meter Signals - Reserved | 401238
38 | 3 | Meter Signals - Reserved | 401239
39 | 3 | Meter Signals - Reserved | 401240
40 | 3 | Meter Signals - Reset Acc 1 | 401241
41 | 3 | Meter Signals - Reset Acc 2 | 401242
42 | 3 | Meter Signals - Reset Acc 3 | 401243
43 | 3 | Meter Signals - Reset Acc 4 | 401244
44 | 3 | Write Daily Archive | 401245
45 | 3 | Write Hourly Archive | 401246
46 | 3 | Meter Signals - Reserved | 401247
47 | 3 | Meter Signals - Reserved | 401248
48 | 3 | Meter Signals - Reserved | 401249
49 | 3 | Meter Signals - Reserved | 401250
50 | 3 | Meter Signals - Reserved | 401251
51 | 3 | Meter Signals - Reserved | 401252
52 | 3 | Analysis is Present | 401253
53 | 3 | Meter Archive Record Fetch | 401254 | (=0 signal not present)
54 | 3 | Meter Archive Record Age | 401255 | (=0 current)
55 | 3 | Meter Archive File Select | 401256 | (=0 daily, 1=hourly)
Meter 4 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Meter Disable | 401401
1 | 4 | Water % | 401402 | Scaled Integer Format
2 | 4 | Temperature | 401403 | Floating Point Format
3 | 4 | Temperature | 401404 | Floating Point Format
4 | 4 | Pressure | 401405 | Floating Point Format
5 | 4 | Pressure | 401406 | Floating Point Format
6 | 4 | Pulse Count | 401407 | Long Integer Format
7 | 4 | Pulse Count | 401408 | Long Integer Format
8 | 4 | Density | 401409 | Floating Point Format
9 | 4 | Density | 401410 | Floating Point Format
10 | 4 | Pulse Frequency | 401411 | Floating Point Format
11 | 4 | Pulse Frequency | 401412 | Floating Point Format
12 | 4 | Molar Analysis - C1 | 401413 | Scaled Integer Format (10000 = 100%)
13 | 4 | Molar Analysis - N2 | 401414 | Scaled Integer Format (10000 = 100%)
14 | 4 | Molar Analysis - CO2 | 401415 | Scaled Integer Format (10000 = 100%)
15 | 4 | Molar Analysis - C2 | 401416 | Scaled Integer Format (10000 = 100%)
16 | 4 | Molar Analysis - C3 | 401417 | Scaled Integer Format (10000 = 100%)
17 | 4 | Molar Analysis - H2O | 401418 | Scaled Integer Format (10000 = 100%)
18 | 4 | Molar Analysis - H2S | 401419 | Scaled Integer Format (10000 = 100%)
19 | 4 | Molar Analysis - H2 | 401420 | Scaled Integer Format (10000 = 100%)
20 | 4 | Molar Analysis - CO | 401421 | Scaled Integer Format (10000 = 100%)
21 | 4 | Molar Analysis - O2 | 401422 | Scaled Integer Format (10000 = 100%)
22 | 4 | Molar Analysis - iC4 | 401423 | Scaled Integer Format (10000 = 100%)
23 | 4 | Molar Analysis - C4 | 401424 | Scaled Integer Format (10000 = 100%)
24 | 4 | Molar Analysis - iC5 | 401425 | Scaled Integer Format (10000 = 100%)
25 | 4 | Molar Analysis - C5 | 401426 | Scaled Integer Format (10000 = 100%)
26 | 4 | Molar Analysis - C6 | 401427 | Scaled Integer Format (10000 = 100%)
27 | 4 | Molar Analysis - C7 | 401428 | Scaled Integer Format (10000 = 100%)
28 | 4 | Molar Analysis - C8 | 401429 | Scaled Integer Format (10000 = 100%)
29 | 4 | Molar Analysis - C9 | 401430 | Scaled Integer Format (10000 = 100%)
30 | 4 | Molar Analysis - C10 | 401431 | Scaled Integer Format (10000 = 100%)
31 | 4 | Molar Analysis - He | 401432 | Scaled Integer Format (10000 = 100%)
32 | 4 | Molar Analysis - Ar | 401433 | Scaled Integer Format (10000 = 100%)
33 | 4 | Molar Analysis - C5 (neo-p) | 401434 | Scaled Integer Format (10000 = 100%)
34 | 4 | Molar Analysis - Ux | 401435 | Scaled Integer Format (10000 = 100%)
35 | 4 | Molar Analysis - Uy | 401436 | Scaled Integer Format (10000 = 100%)
36 | 4 | Meter Signals - Reserved | 401437
37 | 4 | Meter Signals - Reserved | 401438
38 | 4 | Meter Signals - Reserved | 401439
39 | 4 | Meter Signals - Reserved | 401440
40 | 4 | Meter Signals - Reset Acc 1 | 401441
41 | 4 | Meter Signals - Reset Acc 2 | 401442
42 | 4 | Meter Signals - Reset Acc 3 | 401443
43 | 4 | Meter Signals - Reset Acc 4 | 401444
44 | 4 | Write Daily Archive | 401445
45 | 4 | Write Hourly Archive | 401446
46 | 4 | Meter Signals - Reserved | 401447
47 | 4 | Meter Signals - Reserved | 401448
48 | 4 | Meter Signals - Reserved | 401449
49 | 4 | Meter Signals - Reserved | 401450
50 | 4 | Meter Signals - Reserved | 401451
51 | 4 | Meter Signals - Reserved | 401452
52 | 4 | Analysis is Present | 401453
53 | 4 | Meter Archive Record Fetch | 401454 | (=0 signal not present)
54 | 4 | Meter Archive Record Age | 401455 | (=0 current)
55 | 4 | Meter Archive File Select | 401456 | (=0 daily, 1=hourly)
Meter 5 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Meter Disable | 401601
1 | 5 | Water % | 401602 | Scaled Integer Format
2 | 5 | Temperature | 401603 | Floating Point Format
3 | 5 | Temperature | 401604 | Floating Point Format
4 | 5 | Pressure | 401605 | Floating Point Format
5 | 5 | Pressure | 401606 | Floating Point Format
6 | 5 | Differential Pressure | 401607 | Long Integer Format
7 | 5 | Differential Pressure | 401608 | Long Integer Format
8 | 5 | Density | 401609 | Floating Point Format
9 | 5 | Density | 401610 | Floating Point Format
10 | 5 | Pulse Frequency | 401611 | Floating Point Format
11 | 5 | Pulse Frequency | 401612 | Floating Point Format
12 | 5 | Molar Analysis - C1 | 401613 | Scaled Integer Format (10000 = 100%)
13 | 5 | Molar Analysis - N2 | 401614 | Scaled Integer Format (10000 = 100%)
14 | 5 | Molar Analysis - CO2 | 401615 | Scaled Integer Format (10000 = 100%)
15 | 5 | Molar Analysis - C2 | 401616 | Scaled Integer Format (10000 = 100%)
16 | 5 | Molar Analysis - C3 | 401617 | Scaled Integer Format (10000 = 100%)
17 | 5 | Molar Analysis - H2O | 401618 | Scaled Integer Format (10000 = 100%)
18 | 5 | Molar Analysis - H2S | 401619 | Scaled Integer Format (10000 = 100%)
19 | 5 | Molar Analysis - H2 | 401620 | Scaled Integer Format (10000 = 100%)
20 | 5 | Molar Analysis - CO | 401621 | Scaled Integer Format (10000 = 100%)
21 | 5 | Molar Analysis - O2 | 401622 | Scaled Integer Format (10000 = 100%)
22 | 5 | Molar Analysis - iC4 | 401623 | Scaled Integer Format (10000 = 100%)
23 | 5 | Molar Analysis - C4 | 401624 | Scaled Integer Format (10000 = 100%)
24 | 5 | Molar Analysis - iC5 | 401625 | Scaled Integer Format (10000 = 100%)
25 | 5 | Molar Analysis - C5 | 401626 | Scaled Integer Format (10000 = 100%)
26 | 5 | Molar Analysis - C6 | 401627 | Scaled Integer Format (10000 = 100%)
27 | 5 | Molar Analysis - C7 | 401628 | Scaled Integer Format (10000 = 100%)
28 | 5 | Molar Analysis - C8 | 401629 | Scaled Integer Format (10000 = 100%)
29 | 5 | Molar Analysis - C9 | 401630 | Scaled Integer Format (10000 = 100%)
30 | 5 | Molar Analysis - C10 | 401631 | Scaled Integer Format (10000 = 100%)
31 | 5 | Molar Analysis - He | 401632 | Scaled Integer Format (10000 = 100%)
32 | 5 | Molar Analysis - Ar | 401633 | Scaled Integer Format (10000 = 100%)
33 | 5 | Molar Analysis - C5 (neo-p) | 401634 | Scaled Integer Format (10000 = 100%)
34 | 5 | Molar Analysis - Ux | 401635 | Scaled Integer Format (10000 = 100%)
35 | 5 | Molar Analysis - Uy | 401636 | Scaled Integer Format (10000 = 100%)
36 | 5 | Meter Signals - Reserved | 401637
37 | 5 | Meter Signals - Reserved | 401638
38 | 5 | Meter Signals - Reserved | 401639
39 | 5 | Meter Signals - Reserved | 401640
40 | 5 | Meter Signals - Reset Acc 1 | 401641
41 | 5 | Meter Signals - Reset Acc 2 | 401642
42 | 5 | Meter Signals - Reset Acc 3 | 401643
43 | 5 | Meter Signals - Reset Acc 4 | 401644
44 | 5 | Write Daily Archive | 401645
45 | 5 | Write Hourly Archive | 401646
46 | 5 | Meter Signals - Reserved | 401647
47 | 5 | Meter Signals - Reserved | 401648
48 | 5 | Meter Signals - Reserved | 401649
49 | 5 | Meter Signals - Reserved | 401650
50 | 5 | Meter Signals - Reserved | 401651
51 | 5 | Meter Signals - Reserved | 401652
52 | 5 | Analysis is Present | 401653
53 | 5 | Meter Archive Record Fetch | 401654 | (=0 signal not present)
54 | 5 | Meter Archive Record Age | 401655 | (=0 current)
55 | 5 | Meter Archive File Select | 401656 | (=0 daily, 1=hourly)
Meter 6 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Meter Disable | 401801
1 | 6 | Water % | 401802 | Scaled Integer Format
2 | 6 | Temperature | 401803 | Floating Point Format
3 | 6 | Temperature | 401804 | Floating Point Format
4 | 6 | Pressure | 401805 | Floating Point Format
5 | 6 | Pressure | 401806 | Floating Point Format
6 | 6 | Pulse Count | 401807 | Long Integer Format
7 | 6 | Pulse Count | 401808 | Long Integer Format
8 | 6 | Density | 401809 | Floating Point Format
9 | 6 | Density | 401810 | Floating Point Format
10 | 6 | Pulse Frequency | 401811 | Floating Point Format
11 | 6 | Pulse Frequency | 401812 | Floating Point Format
12 | 6 | Molar Analysis - C1 | 401813 | Scaled Integer Format (10000 = 100%)
13 | 6 | Molar Analysis - N2 | 401814 | Scaled Integer Format (10000 = 100%)
14 | 6 | Molar Analysis - CO2 | 401815 | Scaled Integer Format (10000 = 100%)
15 | 6 | Molar Analysis - C2 | 401816 | Scaled Integer Format (10000 = 100%)
16 | 6 | Molar Analysis - C3 | 401817 | Scaled Integer Format (10000 = 100%)
17 | 6 | Molar Analysis - H2O | 401818 | Scaled Integer Format (10000 = 100%)
18 | 6 | Molar Analysis - H2S | 401819 | Scaled Integer Format (10000 = 100%)
19 | 6 | Molar Analysis - H2 | 401820 | Scaled Integer Format (10000 = 100%)
20 | 6 | Molar Analysis - CO | 401821 | Scaled Integer Format (10000 = 100%)
21 | 6 | Molar Analysis - O2 | 401822 | Scaled Integer Format (10000 = 100%)
22 | 6 | Molar Analysis - iC4 | 401823 | Scaled Integer Format (10000 = 100%)
23 | 6 | Molar Analysis - C4 | 401824 | Scaled Integer Format (10000 = 100%)
24 | 6 | Molar Analysis - iC5 | 401825 | Scaled Integer Format (10000 = 100%)
25 | 6 | Molar Analysis - C5 | 401826 | Scaled Integer Format (10000 = 100%)
26 | 6 | Molar Analysis - C6 | 401827 | Scaled Integer Format (10000 = 100%)
27 | 6 | Molar Analysis - C7 | 401828 | Scaled Integer Format (10000 = 100%)
28 | 6 | Molar Analysis - C8 | 401829 | Scaled Integer Format (10000 = 100%)
29 | 6 | Molar Analysis - C9 | 401830 | Scaled Integer Format (10000 = 100%)
30 | 6 | Molar Analysis - C10 | 401831 | Scaled Integer Format (10000 = 100%)
31 | 6 | Molar Analysis - He | 401832 | Scaled Integer Format (10000 = 100%)
32 | 6 | Molar Analysis - Ar | 401833 | Scaled Integer Format (10000 = 100%)
33 | 6 | Molar Analysis - C5 (neo-p) | 401834 | Scaled Integer Format (10000 = 100%)
34 | 6 | Molar Analysis - Ux | 401835 | Scaled Integer Format (10000 = 100%)
35 | 6 | Molar Analysis - Uy | 401836 | Scaled Integer Format (10000 = 100%)
36 | 6 | Meter Signals - Reserved | 401837
37 | 6 | Meter Signals - Reserved | 401838
38 | 6 | Meter Signals - Reserved | 401839
39 | 6 | Meter Signals - Reserved | 401840
40 | 6 | Meter Signals - Reset Acc 1 | 401841
41 | 6 | Meter Signals - Reset Acc 2 | 401842
42 | 6 | Meter Signals - Reset Acc 3 | 401843
43 | 6 | Meter Signals - Reset Acc 4 | 401844
44 | 6 | Write Daily Archive | 401845
45 | 6 | Write Hourly Archive | 401846
46 | 6 | Meter Signals - Reserved | 401847
47 | 6 | Meter Signals - Reserved | 401848
48 | 6 | Meter Signals - Reserved | 401849
49 | 6 | Meter Signals - Reserved | 401850
50 | 6 | Meter Signals - Reserved | 401851
51 | 6 | Meter Signals - Reserved | 401852
52 | 6 | Analysis is Present | 401853
53 | 6 | Meter Archive Record Fetch | 401854 | (=0 signal not present)
54 | 6 | Meter Archive Record Age | 401855 | (=0 current)
55 | 6 | Meter Archive File Select | 401856 | (=0 daily, 1=hourly)
Meter 7 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Meter Disable | 402001
1 | 7 | Water % | 402002 | Scaled Integer Format
2 | 7 | Temperature | 402003 | Floating Point Format
3 | 7 | Temperature | 402004 | Floating Point Format
4 | 7 | Pressure | 402005 | Floating Point Format
5 | 7 | Pressure | 402006 | Floating Point Format
6 | 7 | Pulse Count | 402007 | Long Integer Format
7 | 7 | Pulse Count | 402008 | Long Integer Format
8 | 7 | Density | 402009 | Floating Point Format
9 | 7 | Density | 402010 | Floating Point Format
10 | 7 | Pulse Frequency | 402011 | Floating Point Format
11 | 7 | Pulse Frequency | 402012 | Floating Point Format
12 | 7 | Molar Analysis - C1 | 402013 | Scaled Integer Format (10000 = 100%)
13 | 7 | Molar Analysis - N2 | 402014 | Scaled Integer Format (10000 = 100%)
14 | 7 | Molar Analysis - CO2 | 402015 | Scaled Integer Format (10000 = 100%)
15 | 7 | Molar Analysis - C2 | 402016 | Scaled Integer Format (10000 = 100%)
16 | 7 | Molar Analysis - C3 | 402017 | Scaled Integer Format (10000 = 100%)
17 | 7 | Molar Analysis - H2O | 402018 | Scaled Integer Format (10000 = 100%)
18 | 7 | Molar Analysis - H2S | 402019 | Scaled Integer Format (10000 = 100%)
19 | 7 | Molar Analysis - H2 | 402020 | Scaled Integer Format (10000 = 100%)
20 | 7 | Molar Analysis - CO | 402021 | Scaled Integer Format (10000 = 100%)
21 | 7 | Molar Analysis - O2 | 402022 | Scaled Integer Format (10000 = 100%)
22 | 7 | Molar Analysis - iC4 | 402023 | Scaled Integer Format (10000 = 100%)
23 | 7 | Molar Analysis - C4 | 402024 | Scaled Integer Format (10000 = 100%)
24 | 7 | Molar Analysis - iC5 | 402025 | Scaled Integer Format (10000 = 100%)
25 | 7 | Molar Analysis - C5 | 402026 | Scaled Integer Format (10000 = 100%)
26 | 7 | Molar Analysis - C6 | 402027 | Scaled Integer Format (10000 = 100%)
27 | 7 | Molar Analysis - C7 | 402028 | Scaled Integer Format (10000 = 100%)
28 | 7 | Molar Analysis - C8 | 402029 | Scaled Integer Format (10000 = 100%)
29 | 7 | Molar Analysis - C9 | 402030 | Scaled Integer Format (10000 = 100%)
30 | 7 | Molar Analysis - C10 | 402031 | Scaled Integer Format (10000 = 100%)
31 | 7 | Molar Analysis - He | 402032 | Scaled Integer Format (10000 = 100%)
32 | 7 | Molar Analysis - Ar | 402033 | Scaled Integer Format (10000 = 100%)
33 | 7 | Molar Analysis - C5 (neo-p) | 402034 | Scaled Integer Format (10000 = 100%)
34 | 7 | Molar Analysis - Ux | 402035 | Scaled Integer Format (10000 = 100%)
35 | 7 | Molar Analysis - Uy | 402036 | Scaled Integer Format (10000 = 100%)
36 | 7 | Meter Signals - Reserved | 402037
37 | 7 | Meter Signals - Reserved | 402038
38 | 7 | Meter Signals - Reserved | 402039
39 | 7 | Meter Signals - Reserved | 402040
40 | 7 | Meter Signals - Reset Acc 1 | 402041
41 | 7 | Meter Signals - Reset Acc 2 | 402042
42 | 7 | Meter Signals - Reset Acc 3 | 402043
43 | 7 | Meter Signals - Reset Acc 4 | 402044
44 | 7 | Write Daily Archive | 402045
45 | 7 | Write Hourly Archive | 402046
46 | 7 | Meter Signals - Reserved | 402047
47 | 7 | Meter Signals - Reserved | 402048
48 | 7 | Meter Signals - Reserved | 402049
49 | 7 | Meter Signals - Reserved | 402050
50 | 7 | Meter Signals - Reserved | 402051
51 | 7 | Meter Signals - Reserved | 402052
52 | 7 | Analysis is Present | 402053
53 | 7 | Meter Archive Record Fetch | 402054 | (=0 signal not present)
54 | 7 | Meter Archive Record Age | 402055 | (=0 current)
55 | 7 | Meter Archive File Select | 402056 | (=0 daily, 1=hourly)
Meter 8 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Meter Disable | 402201
1 | 8 | Water % | 402202 | Scaled Integer Format
2 | 8 | Temperature | 402203 | Floating Point Format
3 | 8 | Temperature | 402204 | Floating Point Format
4 | 8 | Pressure | 402205 | Floating Point Format
5 | 8 | Pressure | 402206 | Floating Point Format
6 | 8 | Pulse Count | 402207 | Long Integer Format
7 | 8 | Pulse Count | 402208 | Long Integer Format
8 | 8 | Density | 402209 | Floating Point Format
9 | 8 | Density | 402210 | Floating Point Format
10 | 8 | Pulse Frequency | 402211 | Floating Point Format
11 | 8 | Pulse Frequency | 402212 | Floating Point Format
12 | 8 | Molar Analysis - C1 | 402213 | Scaled Integer Format (10000 = 100%)
13 | 8 | Molar Analysis - N2 | 402214 | Scaled Integer Format (10000 = 100%)
14 | 8 | Molar Analysis - CO2 | 402215 | Scaled Integer Format (10000 = 100%)
15 | 8 | Molar Analysis - C2 | 402216 | Scaled Integer Format (10000 = 100%)
16 | 8 | Molar Analysis - C3 | 402217 | Scaled Integer Format (10000 = 100%)
17 | 8 | Molar Analysis - H2O | 402218 | Scaled Integer Format (10000 = 100%)
18 | 8 | Molar Analysis - H2S | 402219 | Scaled Integer Format (10000 = 100%)
19 | 8 | Molar Analysis - H2 | 402220 | Scaled Integer Format (10000 = 100%)
20 | 8 | Molar Analysis - CO | 402221 | Scaled Integer Format (10000 = 100%)
21 | 8 | Molar Analysis - O2 | 402222 | Scaled Integer Format (10000 = 100%)
22 | 8 | Molar Analysis - iC4 | 402223 | Scaled Integer Format (10000 = 100%)
23 | 8 | Molar Analysis - C4 | 402224 | Scaled Integer Format (10000 = 100%)
24 | 8 | Molar Analysis - iC5 | 402225 | Scaled Integer Format (10000 = 100%)
25 | 8 | Molar Analysis - C5 | 402226 | Scaled Integer Format (10000 = 100%)
26 | 8 | Molar Analysis - C6 | 402227 | Scaled Integer Format (10000 = 100%)
27 | 8 | Molar Analysis - C7 | 402228 | Scaled Integer Format (10000 = 100%)
28 | 8 | Molar Analysis - C8 | 402229 | Scaled Integer Format (10000 = 100%)
29 | 8 | Molar Analysis - C9 | 402230 | Scaled Integer Format (10000 = 100%)
30 | 8 | Molar Analysis - C10 | 402231 | Scaled Integer Format (10000 = 100%)
31 | 8 | Molar Analysis - He | 402232 | Scaled Integer Format (10000 = 100%)
32 | 8 | Molar Analysis - Ar | 402233 | Scaled Integer Format (10000 = 100%)
33 | 8 | Molar Analysis - C5 (neo-p) | 402234 | Scaled Integer Format (10000 = 100%)
34 | 8 | Molar Analysis - Ux | 402235 | Scaled Integer Format (10000 = 100%)
35 | 8 | Molar Analysis - Uy | 402236 | Scaled Integer Format (10000 = 100%)
36 | 8 | Meter Signals - Reserved | 402237
37 | 8 | Meter Signals - Reserved | 402238
38 | 8 | Meter Signals - Reserved | 402239
39 | 8 | Meter Signals - Reserved | 402240
40 | 8 | Meter Signals - Reset Acc 1 | 402241
41 | 8 | Meter Signals - Reset Acc 2 | 402242
42 | 8 | Meter Signals - Reset Acc 3 | 402243
43 | 8 | Meter Signals - Reset Acc 4 | 402244
44 | 8 | Write Daily Archive | 402245
45 | 8 | Write Hourly Archive | 402246
46 | 8 | Meter Signals - Reserved | 402247
47 | 8 | Meter Signals - Reserved | 402248
48 | 8 | Meter Signals - Reserved | 402249
49 | 8 | Meter Signals - Reserved | 402250
50 | 8 | Meter Signals - Reserved | 402251
51 | 8 | Meter Signals - Reserved | 402252
52 | 8 | Analysis is Present | 402253
53 | 8 | Meter Archive Record Fetch | 402254 | (=0 signal not present)
54 | 8 | Meter Archive Record Age | 402255 | (=0 current)
55 | 8 | Meter Archive File Select | 402256 | (=0 daily, 1=hourly)
Meter 9 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Meter Disable | 402401
1 | 9 | Water % | 402402 | Scaled Integer Format
2 | 9 | Temperature | 402403 | Floating Point Format
3 | 9 | Temperature | 402404 | Floating Point Format
4 | 9 | Pressure | 402405 | Floating Point Format
5 | 9 | Pressure | 402406 | Floating Point Format
6 | 9 | Pulse Count | 402407 | Long Integer Format
7 | 9 | Pulse Count | 402408 | Long Integer Format
8 | 9 | Density | 402409 | Floating Point Format
9 | 9 | Density | 402410 | Floating Point Format
10 | 9 | Pulse Frequency | 402411 | Floating Point Format
11 | 9 | Pulse Frequency | 402412 | Floating Point Format
12 | 9 | Molar Analysis - C1 | 402413 | Scaled Integer Format (10000 = 100%)
13 | 9 | Molar Analysis - N2 | 402414 | Scaled Integer Format (10000 = 100%)
14 | 9 | Molar Analysis - CO2 | 402415 | Scaled Integer Format (10000 = 100%)
15 | 9 | Molar Analysis - C2 | 402416 | Scaled Integer Format (10000 = 100%)
16 | 9 | Molar Analysis - C3 | 402417 | Scaled Integer Format (10000 = 100%)
17 | 9 | Molar Analysis - H2O | 402418 | Scaled Integer Format (10000 = 100%)
18 | 9 | Molar Analysis - H2S | 402419 | Scaled Integer Format (10000 = 100%)
19 | 9 | Molar Analysis - H2 | 402420 | Scaled Integer Format (10000 = 100%)
20 | 9 | Molar Analysis - CO | 402421 | Scaled Integer Format (10000 = 100%)
21 | 9 | Molar Analysis - O2 | 402422 | Scaled Integer Format (10000 = 100%)
22 | 9 | Molar Analysis - iC4 | 402423 | Scaled Integer Format (10000 = 100%)
23 | 9 | Molar Analysis - C4 | 402424 | Scaled Integer Format (10000 = 100%)
24 | 9 | Molar Analysis - iC5 | 402425 | Scaled Integer Format (10000 = 100%)
25 | 9 | Molar Analysis - C5 | 402426 | Scaled Integer Format (10000 = 100%)
26 | 9 | Molar Analysis - C6 | 402427 | Scaled Integer Format (10000 = 100%)
27 | 9 | Molar Analysis - C7 | 402428 | Scaled Integer Format (10000 = 100%)
28 | 9 | Molar Analysis - C8 | 402429 | Scaled Integer Format (10000 = 100%)
29 | 9 | Molar Analysis - C9 | 402430 | Scaled Integer Format (10000 = 100%)
30 | 9 | Molar Analysis - C10 | 402431 | Scaled Integer Format (10000 = 100%)
31 | 9 | Molar Analysis - He | 402432 | Scaled Integer Format (10000 = 100%)
32 | 9 | Molar Analysis - Ar | 402433 | Scaled Integer Format (10000 = 100%)
33 | 9 | Molar Analysis - C5 (neo-p) | 402434 | Scaled Integer Format (10000 = 100%)
34 | 9 | Molar Analysis - Ux | 402435 | Scaled Integer Format (10000 = 100%)
35 | 9 | Molar Analysis - Uy | 402436 | Scaled Integer Format (10000 = 100%)
36 | 9 | Meter Signals - Reserved | 402437
37 | 9 | Meter Signals - Reserved | 402438
38 | 9 | Meter Signals - Reserved | 402439
39 | 9 | Meter Signals - Reserved | 402440
40 | 9 | Meter Signals - Reset Acc 1 | 402441
41 | 9 | Meter Signals - Reset Acc 2 | 402442
42 | 9 | Meter Signals - Reset Acc 3 | 402443
43 | 9 | Meter Signals - Reset Acc 4 | 402444
44 | 9 | Write Daily Archive | 402445
45 | 9 | Write Hourly Archive | 402446
46 | 9 | Meter Signals - Reserved | 402447
47 | 9 | Meter Signals - Reserved | 402448
48 | 9 | Meter Signals - Reserved | 402449
49 | 9 | Meter Signals - Reserved | 402450
50 | 9 | Meter Signals - Reserved | 402451
51 | 9 | Meter Signals - Reserved | 402452
52 | 9 | Analysis is Present | 402453
53 | 9 | Meter Archive Record Fetch | 402454 | (=0 signal not present)
54 | 9 | Meter Archive Record Age | 402455 | (=0 current)
55 | 9 | Meter Archive File Select | 402456 | (=0 daily, 1=hourly)
Meter 10 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Meter Disable | 402601
1 | 10 | Water % | 402602 | Scaled Integer Format
2 | 10 | Temperature | 402603 | Floating Point Format
3 | 10 | Temperature | 402604 | Floating Point Format
4 | 10 | Pressure | 402605 | Floating Point Format
5 | 10 | Pressure | 402606 | Floating Point Format
6 | 10 | Pulse Count | 402607 | Long Integer Format
7 | 10 | Pulse Count | 402608 | Long Integer Format
8 | 10 | Density | 402609 | Floating Point Format
9 | 10 | Density | 402610 | Floating Point Format
10 | 10 | Pulse Frequency | 402611 | Floating Point Format
11 | 10 | Pulse Frequency | 402612 | Floating Point Format
12 | 10 | Molar Analysis - C1 | 402613 | Scaled Integer Format (10000 = 100%)
13 | 10 | Molar Analysis - N2 | 402614 | Scaled Integer Format (10000 = 100%)
14 | 10 | Molar Analysis - CO2 | 402615 | Scaled Integer Format (10000 = 100%)
15 | 10 | Molar Analysis - C2 | 402616 | Scaled Integer Format (10000 = 100%)
16 | 10 | Molar Analysis - C3 | 402617 | Scaled Integer Format (10000 = 100%)
17 | 10 | Molar Analysis - H2O | 402618 | Scaled Integer Format (10000 = 100%)
18 | 10 | Molar Analysis - H2S | 402619 | Scaled Integer Format (10000 = 100%)
19 | 10 | Molar Analysis - H2 | 402620 | Scaled Integer Format (10000 = 100%)
20 | 10 | Molar Analysis - CO | 402621 | Scaled Integer Format (10000 = 100%)
21 | 10 | Molar Analysis - O2 | 402622 | Scaled Integer Format (10000 = 100%)
22 | 10 | Molar Analysis - iC4 | 402623 | Scaled Integer Format (10000 = 100%)
23 | 10 | Molar Analysis - C4 | 402624 | Scaled Integer Format (10000 = 100%)
24 | 10 | Molar Analysis - iC5 | 402625 | Scaled Integer Format (10000 = 100%)
25 | 10 | Molar Analysis - C5 | 402626 | Scaled Integer Format (10000 = 100%)
26 | 10 | Molar Analysis - C6 | 402627 | Scaled Integer Format (10000 = 100%)
27 | 10 | Molar Analysis - C7 | 402628 | Scaled Integer Format (10000 = 100%)
28 | 10 | Molar Analysis - C8 | 402629 | Scaled Integer Format (10000 = 100%)
29 | 10 | Molar Analysis - C9 | 402630 | Scaled Integer Format (10000 = 100%)
30 | 10 | Molar Analysis - C10 | 402631 | Scaled Integer Format (10000 = 100%)
31 | 10 | Molar Analysis - He | 402632 | Scaled Integer Format (10000 = 100%)
32 | 10 | Molar Analysis - Ar | 402633 | Scaled Integer Format (10000 = 100%)
33 | 10 | Molar Analysis - C5 (neo-p) | 402634 | Scaled Integer Format (10000 = 100%)
34 | 10 | Molar Analysis - Ux | 402635 | Scaled Integer Format (10000 = 100%)
35 | 10 | Molar Analysis - Uy | 402636 | Scaled Integer Format (10000 = 100%)
36 | 10 | Meter Signals - Reserved | 402637
37 | 10 | Meter Signals - Reserved | 402638
38 | 10 | Meter Signals - Reserved | 402639
39 | 10 | Meter Signals - Reserved | 402640
40 | 10 | Meter Signals - Reset Acc 1 | 402641
41 | 10 | Meter Signals - Reset Acc 2 | 402642
42 | 10 | Meter Signals - Reset Acc 3 | 402643
43 | 10 | Meter Signals - Reset Acc 4 | 402644
44 | 10 | Write Daily Archive | 402645
45 | 10 | Write Hourly Archive | 402646
46 | 10 | Meter Signals - Reserved | 402647
47 | 10 | Meter Signals - Reserved | 402648
48 | 10 | Meter Signals - Reserved | 402649
49 | 10 | Meter Signals - Reserved | 402650
50 | 10 | Meter Signals - Reserved | 402651
51 | 10 | Meter Signals - Reserved | 402652
52 | 10 | Analysis is Present | 402653
53 | 10 | Meter Archive Record Fetch | 402654 | (=0 signal not present)
54 | 10 | Meter Archive Record Age | 402655 | (=0 current)
55 | 10 | Meter Archive File Select | 402656 | (=0 daily, 1=hourly)
Meter 11 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Meter Disable | 402801
1 | 11 | Water % | 402802 | Scaled Integer Format
2 | 11 | Temperature | 402803 | Floating Point Format
3 | 11 | Temperature | 402804 | Floating Point Format
4 | 11 | Pressure | 402805 | Floating Point Format
5 | 11 | Pressure | 402806 | Floating Point Format
6 | 11 | Pulse Count | 402807 | Long Integer Format
7 | 11 | Pulse Count | 402808 | Long Integer Format
8 | 11 | Density | 402809 | Floating Point Format
9 | 11 | Density | 402810 | Floating Point Format
10 | 11 | Pulse Frequency | 402811 | Floating Point Format
11 | 11 | Pulse Frequency | 402812 | Floating Point Format
12 | 11 | Molar Analysis - C1 | 402813 | Scaled Integer Format (10000 = 100%)
13 | 11 | Molar Analysis - N2 | 402814 | Scaled Integer Format (10000 = 100%)
14 | 11 | Molar Analysis - CO2 | 402815 | Scaled Integer Format (10000 = 100%)
15 | 11 | Molar Analysis - C2 | 402816 | Scaled Integer Format (10000 = 100%)
16 | 11 | Molar Analysis - C3 | 402817 | Scaled Integer Format (10000 = 100%)
17 | 11 | Molar Analysis - H2O | 402818 | Scaled Integer Format (10000 = 100%)
18 | 11 | Molar Analysis - H2S | 402819 | Scaled Integer Format (10000 = 100%)
19 | 11 | Molar Analysis - H2 | 402820 | Scaled Integer Format (10000 = 100%)
20 | 11 | Molar Analysis - CO | 402821 | Scaled Integer Format (10000 = 100%)
21 | 11 | Molar Analysis - O2 | 402822 | Scaled Integer Format (10000 = 100%)
22 | 11 | Molar Analysis - iC4 | 402823 | Scaled Integer Format (10000 = 100%)
23 | 11 | Molar Analysis - C4 | 402824 | Scaled Integer Format (10000 = 100%)
24 | 11 | Molar Analysis - iC5 | 402825 | Scaled Integer Format (10000 = 100%)
25 | 11 | Molar Analysis - C5 | 402826 | Scaled Integer Format (10000 = 100%)
26 | 11 | Molar Analysis - C6 | 402827 | Scaled Integer Format (10000 = 100%)
27 | 11 | Molar Analysis - C7 | 402828 | Scaled Integer Format (10000 = 100%)
28 | 11 | Molar Analysis - C8 | 402829 | Scaled Integer Format (10000 = 100%)
29 | 11 | Molar Analysis - C9 | 402830 | Scaled Integer Format (10000 = 100%)
30 | 11 | Molar Analysis - C10 | 402831 | Scaled Integer Format (10000 = 100%)
31 | 11 | Molar Analysis - He | 402832 | Scaled Integer Format (10000 = 100%)
32 | 11 | Molar Analysis - Ar | 402833 | Scaled Integer Format (10000 = 100%)
33 | 11 | Molar Analysis - C5 (neo-p) | 402834 | Scaled Integer Format (10000 = 100%)
34 | 11 | Molar Analysis - Ux | 402835 | Scaled Integer Format (10000 = 100%)
35 | 11 | Molar Analysis - Uy | 402836 | Scaled Integer Format (10000 = 100%)
36 | 11 | Meter Signals - Reserved | 402837
37 | 11 | Meter Signals - Reserved | 402838
38 | 11 | Meter Signals - Reserved | 402839
39 | 11 | Meter Signals - Reserved | 402840
40 | 11 | Meter Signals - Reset Acc 1 | 402841
41 | 11 | Meter Signals - Reset Acc 2 | 402842
42 | 11 | Meter Signals - Reset Acc 3 | 402843
43 | 11 | Meter Signals - Reset Acc 4 | 402844
44 | 11 | Write Daily Archive | 402845
45 | 11 | Write Hourly Archive | 402846
46 | 11 | Meter Signals - Reserved | 402847
47 | 11 | Meter Signals - Reserved | 402848
48 | 11 | Meter Signals - Reserved | 402849
49 | 11 | Meter Signals - Reserved | 402850
50 | 11 | Meter Signals - Reserved | 402851
51 | 11 | Meter Signals - Reserved | 402852
52 | 11 | Analysis is Present | 402853
53 | 11 | Meter Archive Record Fetch | 402854 | (=0 signal not present)
54 | 11 | Meter Archive Record Age | 402855 | (=0 current)
55 | 11 | Meter Archive File Select | 402856 | (=0 daily, 1=hourly)
Meter 12 Variables Pulse & Gas
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Meter Disable | 403001
1 | 12 | Water % | 403002 | Scaled Integer Format
2 | 12 | Temperature | 403003 | Floating Point Format
3 | 12 | Temperature | 403004 | Floating Point Format
4 | 12 | Pressure | 403005 | Floating Point Format
5 | 12 | Pressure | 403006 | Floating Point Format
6 | 12 | Pulse Count | 403007 | Long Integer Format
7 | 12 | Pulse Count | 403008 | Long Integer Format
8 | 12 | Density | 403009 | Floating Point Format
9 | 12 | Density | 403010 | Floating Point Format
10 | 12 | Pulse Frequency | 403011 | Floating Point Format
11 | 12 | Pulse Frequency | 403012 | Floating Point Format
12 | 12 | Molar Analysis - C1 | 403013 | Scaled Integer Format (10000 = 100%)
13 | 12 | Molar Analysis - N2 | 403014 | Scaled Integer Format (10000 = 100%)
14 | 12 | Molar Analysis - CO2 | 403015 | Scaled Integer Format (10000 = 100%)
15 | 12 | Molar Analysis - C2 | 403016 | Scaled Integer Format (10000 = 100%)
16 | 12 | Molar Analysis - C3 | 403017 | Scaled Integer Format (10000 = 100%)
17 | 12 | Molar Analysis - H2O | 403018 | Scaled Integer Format (10000 = 100%)
18 | 12 | Molar Analysis - H2S | 403019 | Scaled Integer Format (10000 = 100%)
19 | 12 | Molar Analysis - H2 | 403020 | Scaled Integer Format (10000 = 100%)
20 | 12 | Molar Analysis - CO | 403021 | Scaled Integer Format (10000 = 100%)
21 | 12 | Molar Analysis - O2 | 403022 | Scaled Integer Format (10000 = 100%)
22 | 12 | Molar Analysis - iC4 | 403023 | Scaled Integer Format (10000 = 100%)
23 | 12 | Molar Analysis - C4 | 403024 | Scaled Integer Format (10000 = 100%)
24 | 12 | Molar Analysis - iC5 | 403025 | Scaled Integer Format (10000 = 100%)
25 | 12 | Molar Analysis - C5 | 403026 | Scaled Integer Format (10000 = 100%)
26 | 12 | Molar Analysis - C6 | 403027 | Scaled Integer Format (10000 = 100%)
27 | 12 | Molar Analysis - C7 | 403028 | Scaled Integer Format (10000 = 100%)
28 | 12 | Molar Analysis - C8 | 403029 | Scaled Integer Format (10000 = 100%)
29 | 12 | Molar Analysis - C9 | 403030 | Scaled Integer Format (10000 = 100%)
30 | 12 | Molar Analysis - C10 | 403031 | Scaled Integer Format (10000 = 100%)
31 | 12 | Molar Analysis - He | 403032 | Scaled Integer Format (10000 = 100%)
32 | 12 | Molar Analysis - Ar | 403033 | Scaled Integer Format (10000 = 100%)
33 | 12 | Molar Analysis - C5 (neo-p) | 403034 | Scaled Integer Format (10000 = 100%)
34 | 12 | Molar Analysis - Ux | 403035 | Scaled Integer Format (10000 = 100%)
35 | 12 | Molar Analysis - Uy | 403036 | Scaled Integer Format (10000 = 100%)
36 | 12 | Meter Signals - Reserved | 403037
37 | 12 | Meter Signals - Reserved | 403038
38 | 12 | Meter Signals - Reserved | 403039
39 | 12 | Meter Signals - Reserved | 403040
40 | 12 | Meter Signals - Reset Acc 1 | 403041
41 | 12 | Meter Signals - Reset Acc 2 | 403042
42 | 12 | Meter Signals - Reset Acc 3 | 403043
43 | 12 | Meter Signals - Reset Acc 4 | 403044
44 | 12 | Write Daily Archive | 403045
45 | 12 | Write Hourly Archive | 403046
46 | 12 | Meter Signals - Reserved | 403047
47 | 12 | Meter Signals - Reserved | 403048
48 | 12 | Meter Signals - Reserved | 403049
49 | 12 | Meter Signals - Reserved | 403050
50 | 12 | Meter Signals - Reserved | 403051
51 | 12 | Meter Signals - Reserved | 403052
52 | 12 | Analysis is Present | 403053
53 | 12 | Meter Archive Record Fetch | 403054 | (=0 signal not present)
54 | 12 | Meter Archive Record Age | 403055 | (=0 current)
55 | 12 | Meter Archive File Select | 403056 | (=0 daily, 1=hourly)
Meter 13 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Meter Disable | 403201
1 | 13 | Water % | 403202 | Scaled Integer Format
2 | 13 | Temperature | 403203 | Floating Point Format
3 | 13 | Temperature | 403204 | Floating Point Format
4 | 13 | Pressure | 403205 | Floating Point Format
5 | 13 | Pressure | 403206 | Floating Point Format
6 | 13 | Pulse Count | 403207 | Long Integer Format
7 | 13 | Pulse Count | 403208 | Long Integer Format
8 | 13 | Density | 403209 | Floating Point Format
9 | 13 | Density | 403210 | Floating Point Format
10 | 13 | Pulse Frequency | 403211 | Floating Point Format
11 | 13 | Pulse Frequency | 403212 | Floating Point Format
12 | 13 | Molar Analysis - C1 | 403213 | Scaled Integer Format (10000 = 100%)
13 | 13 | Molar Analysis - N2 | 403214 | Scaled Integer Format (10000 = 100%)
14 | 13 | Molar Analysis - CO2 | 403215 | Scaled Integer Format (10000 = 100%)
15 | 13 | Molar Analysis - C2 | 403216 | Scaled Integer Format (10000 = 100%)
16 | 13 | Molar Analysis - C3 | 403217 | Scaled Integer Format (10000 = 100%)
17 | 13 | Molar Analysis - H2O | 403218 | Scaled Integer Format (10000 = 100%)
18 | 13 | Molar Analysis - H2S | 403219 | Scaled Integer Format (10000 = 100%)
19 | 13 | Molar Analysis - H2 | 403220 | Scaled Integer Format (10000 = 100%)
20 | 13 | Molar Analysis - CO | 403221 | Scaled Integer Format (10000 = 100%)
21 | 13 | Molar Analysis - O2 | 403222 | Scaled Integer Format (10000 = 100%)
22 | 13 | Molar Analysis - iC4 | 403223 | Scaled Integer Format (10000 = 100%)
23 | 13 | Molar Analysis - C4 | 403224 | Scaled Integer Format (10000 = 100%)
24 | 13 | Molar Analysis - iC5 | 403225 | Scaled Integer Format (10000 = 100%)
25 | 13 | Molar Analysis - C5 | 403226 | Scaled Integer Format (10000 = 100%)
26 | 13 | Molar Analysis - C6 | 403227 | Scaled Integer Format (10000 = 100%)
27 | 13 | Molar Analysis - C7 | 403228 | Scaled Integer Format (10000 = 100%)
28 | 13 | Molar Analysis - C8 | 403229 | Scaled Integer Format (10000 = 100%)
29 | 13 | Molar Analysis - C9 | 403230 | Scaled Integer Format (10000 = 100%)
30 | 13 | Molar Analysis - C10 | 403231 | Scaled Integer Format (10000 = 100%)
31 | 13 | Molar Analysis - He | 403232 | Scaled Integer Format (10000 = 100%)
32 | 13 | Molar Analysis - Ar | 403233 | Scaled Integer Format (10000 = 100%)
33 | 13 | Molar Analysis - C5 (neo-p) | 403234 | Scaled Integer Format (10000 = 100%)
34 | 13 | Molar Analysis - Ux | 403235 | Scaled Integer Format (10000 = 100%)
35 | 13 | Molar Analysis - Uy | 403236 | Scaled Integer Format (10000 = 100%)
36 | 13 | Meter Signals - Reserved | 403237
37 | 13 | Meter Signals - Reserved | 403238
38 | 13 | Meter Signals - Reserved | 403239
39 | 13 | Meter Signals - Reserved | 403240
40 | 13 | Meter Signals - Reset Acc 1 | 403241
41 | 13 | Meter Signals - Reset Acc 2 | 403242
42 | 13 | Meter Signals - Reset Acc 3 | 403243
43 | 13 | Meter Signals - Reset Acc 4 | 403244
44 | 13 | Write Daily Archive | 403245
45 | 13 | Write Hourly Archive | 403246
46 | 13 | Meter Signals - Reserved | 403247
47 | 13 | Meter Signals - Reserved | 403248
48 | 13 | Meter Signals - Reserved | 403249
49 | 13 | Meter Signals - Reserved | 403250
50 | 13 | Meter Signals - Reserved | 403251
51 | 13 | Meter Signals - Reserved | 403252
52 | 13 | Analysis is Present | 403253
53 | 13 | Meter Archive Record Fetch | 403254 | (=0 signal not present)
54 | 13 | Meter Archive Record Age | 403255 | (=0 current)
55 | 13 | Meter Archive File Select | 403256 | (=0 daily, 1=hourly)
Meter 14 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Meter Disable | 403401
1 | 14 | Water % | 403402 | Scaled Integer Format
2 | 14 | Temperature | 403403 | Floating Point Format
3 | 14 | Temperature | 403404 | Floating Point Format
4 | 14 | Pressure | 403405 | Floating Point Format
5 | 14 | Pressure | 403406 | Floating Point Format
6 | 14 | Pulse Count | 403407 | Long Integer Format
7 | 14 | Pulse Count | 403408 | Long Integer Format
8 | 14 | Density | 403409 | Floating Point Format
9 | 14 | Density | 403410 | Floating Point Format
10 | 14 | Pulse Frequency | 403411 | Floating Point Format
11 | 14 | Pulse Frequency | 403412 | Floating Point Format
12 | 14 | Molar Analysis - C1 | 403413 | Scaled Integer Format (10000 = 100%)
13 | 14 | Molar Analysis - N2 | 403414 | Scaled Integer Format (10000 = 100%)
14 | 14 | Molar Analysis - CO2 | 403415 | Scaled Integer Format (10000 = 100%)
15 | 14 | Molar Analysis - C2 | 403416 | Scaled Integer Format (10000 = 100%)
16 | 14 | Molar Analysis - C3 | 403417 | Scaled Integer Format (10000 = 100%)
17 | 14 | Molar Analysis - H2O | 403418 | Scaled Integer Format (10000 = 100%)
18 | 14 | Molar Analysis - H2S | 403419 | Scaled Integer Format (10000 = 100%)
19 | 14 | Molar Analysis - H2 | 403420 | Scaled Integer Format (10000 = 100%)
20 | 14 | Molar Analysis - CO | 403421 | Scaled Integer Format (10000 = 100%)
21 | 14 | Molar Analysis - O2 | 403422 | Scaled Integer Format (10000 = 100%)
22 | 14 | Molar Analysis - iC4 | 403423 | Scaled Integer Format (10000 = 100%)
23 | 14 | Molar Analysis - C4 | 403424 | Scaled Integer Format (10000 = 100%)
24 | 14 | Molar Analysis - iC5 | 403425 | Scaled Integer Format (10000 = 100%)
25 | 14 | Molar Analysis - C5 | 403426 | Scaled Integer Format (10000 = 100%)
26 | 14 | Molar Analysis - C6 | 403427 | Scaled Integer Format (10000 = 100%)
27 | 14 | Molar Analysis - C7 | 403428 | Scaled Integer Format (10000 = 100%)
28 | 14 | Molar Analysis - C8 | 403429 | Scaled Integer Format (10000 = 100%)
29 | 14 | Molar Analysis - C9 | 403430 | Scaled Integer Format (10000 = 100%)
30 | 14 | Molar Analysis - C10 | 403431 | Scaled Integer Format (10000 = 100%)
31 | 14 | Molar Analysis - He | 403432 | Scaled Integer Format (10000 = 100%)
32 | 14 | Molar Analysis - Ar | 403433 | Scaled Integer Format (10000 = 100%)
33 | 14 | Molar Analysis - C5 (neo-p) | 403434 | Scaled Integer Format (10000 = 100%)
34 | 14 | Molar Analysis - Ux | 403435 | Scaled Integer Format (10000 = 100%)
35 | 14 | Molar Analysis - Uy | 403436 | Scaled Integer Format (10000 = 100%)
36 | 14 | Meter Signals - Reserved | 403437
37 | 14 | Meter Signals - Reserved | 403438
38 | 14 | Meter Signals - Reserved | 403439
39 | 14 | Meter Signals - Reserved | 403440
40 | 14 | Meter Signals - Reset Acc 1 | 403441
41 | 14 | Meter Signals - Reset Acc 2 | 403442
42 | 14 | Meter Signals - Reset Acc 3 | 403443
43 | 14 | Meter Signals - Reset Acc 4 | 403444
44 | 14 | Write Daily Archive | 403445
45 | 14 | Write Hourly Archive | 403446
46 | 14 | Meter Signals - Reserved | 403447
47 | 14 | Meter Signals - Reserved | 403448
48 | 14 | Meter Signals - Reserved | 403449
49 | 14 | Meter Signals - Reserved | 403450
50 | 14 | Meter Signals - Reserved | 403451
51 | 14 | Meter Signals - Reserved | 403452
52 | 14 | Analysis is Present | 403453
53 | 14 | Meter Archive Record Fetch | 403454 | (=0 signal not present)
54 | 14 | Meter Archive Record Age | 403455 | (=0 current)
55 | 14 | Meter Archive File Select | 403456 | (=0 daily, 1=hourly)
Meter 15 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Meter Disable | 403601
1 | 15 | Water % | 403602 | Scaled Integer Format
2 | 15 | Temperature | 403603 | Floating Point Format
3 | 15 | Temperature | 403604 | Floating Point Format
4 | 15 | Pressure | 403605 | Floating Point Format
5 | 15 | Pressure | 403606 | Floating Point Format
6 | 15 | Pulse Count | 403607 | Long Integer Format
7 | 15 | Pulse Count | 403608 | Long Integer Format
8 | 15 | Density | 403609 | Floating Point Format
9 | 15 | Density | 403610 | Floating Point Format
10 | 15 | Pulse Frequency | 403611 | Floating Point Format
11 | 15 | Pulse Frequency | 403612 | Floating Point Format
12 | 15 | Molar Analysis - C1 | 403613 | Scaled Integer Format (10000 = 100%)
13 | 15 | Molar Analysis - N2 | 403614 | Scaled Integer Format (10000 = 100%)
14 | 15 | Molar Analysis - CO2 | 403615 | Scaled Integer Format (10000 = 100%)
15 | 15 | Molar Analysis - C2 | 403616 | Scaled Integer Format (10000 = 100%)
16 | 15 | Molar Analysis - C3 | 403617 | Scaled Integer Format (10000 = 100%)
17 | 15 | Molar Analysis - H2O | 403618 | Scaled Integer Format (10000 = 100%)
18 | 15 | Molar Analysis - H2S | 403619 | Scaled Integer Format (10000 = 100%)
19 | 15 | Molar Analysis - H2 | 403620 | Scaled Integer Format (10000 = 100%)
20 | 15 | Molar Analysis - CO | 403621 | Scaled Integer Format (10000 = 100%)
21 | 15 | Molar Analysis - O2 | 403622 | Scaled Integer Format (10000 = 100%)
22 | 15 | Molar Analysis - iC4 | 403623 | Scaled Integer Format (10000 = 100%)
23 | 15 | Molar Analysis - C4 | 403624 | Scaled Integer Format (10000 = 100%)
24 | 15 | Molar Analysis - iC5 | 403625 | Scaled Integer Format (10000 = 100%)
25 | 15 | Molar Analysis - C5 | 403626 | Scaled Integer Format (10000 = 100%)
26 | 15 | Molar Analysis - C6 | 403627 | Scaled Integer Format (10000 = 100%)
27 | 15 | Molar Analysis - C7 | 403628 | Scaled Integer Format (10000 = 100%)
28 | 15 | Molar Analysis - C8 | 403629 | Scaled Integer Format (10000 = 100%)
29 | 15 | Molar Analysis - C9 | 403630 | Scaled Integer Format (10000 = 100%)
30 | 15 | Molar Analysis - C10 | 403631 | Scaled Integer Format (10000 = 100%)
31 | 15 | Molar Analysis - He | 403632 | Scaled Integer Format (10000 = 100%)
32 | 15 | Molar Analysis - Ar | 403633 | Scaled Integer Format (10000 = 100%)
33 | 15 | Molar Analysis - C5 (neo-p) | 403634 | Scaled Integer Format (10000 = 100%)
34 | 15 | Molar Analysis - Ux | 403635 | Scaled Integer Format (10000 = 100%)
35 | 15 | Molar Analysis - Uy | 403636 | Scaled Integer Format (10000 = 100%)
36 | 15 | Meter Signals - Reserved | 403637
37 | 15 | Meter Signals - Reserved | 403638
38 | 15 | Meter Signals - Reserved | 403639
39 | 15 | Meter Signals - Reserved | 403640
40 | 15 | Meter Signals - Reset Acc 1 | 403641
41 | 15 | Meter Signals - Reset Acc 2 | 403642
42 | 15 | Meter Signals - Reset Acc 3 | 403643
43 | 15 | Meter Signals - Reset Acc 4 | 403644
44 | 15 | Write Daily Archive | 403645
45 | 15 | Write Hourly Archive | 403646
46 | 15 | Meter Signals - Reserved | 403647
47 | 15 | Meter Signals - Reserved | 403648
48 | 15 | Meter Signals - Reserved | 403649
49 | 15 | Meter Signals - Reserved | 403650
50 | 15 | Meter Signals - Reserved | 403651
51 | 15 | Meter Signals - Reserved | 403652
52 | 15 | Analysis is Present | 403653
53 | 15 | Meter Archive Record Fetch | 403654 | (=0 signal not present)
54 | 15 | Meter Archive Record Age | 403655 | (=0 current)
55 | 15 | Meter Archive File Select | 403656 | (=0 daily, 1=hourly)
Meter 16 Variables Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Meter Disable | 403801
1 | 16 | Water % | 403802 | Scaled Integer Format
2 | 16 | Temperature | 403803 | Floating Point Format
3 | 16 | Temperature | 403804 | Floating Point Format
4 | 16 | Pressure | 403805 | Floating Point Format
5 | 16 | Pressure | 403806 | Floating Point Format
6 | 16 | Pulse Count | 403807 | Long Integer Format
7 | 16 | Pulse Count | 403808 | Long Integer Format
8 | 16 | Density | 403809 | Floating Point Format
9 | 16 | Density | 403810 | Floating Point Format
10 | 16 | Pulse Frequency | 403811 | Floating Point Format
11 | 16 | Pulse Frequency | 403812 | Floating Point Format
12 | 16 | Molar Analysis - C1 | 403813 | Scaled Integer Format (10000 = 100%)
13 | 16 | Molar Analysis - N2 | 403814 | Scaled Integer Format (10000 = 100%)
14 | 16 | Molar Analysis - CO2 | 403815 | Scaled Integer Format (10000 = 100%)
15 | 16 | Molar Analysis - C2 | 403816 | Scaled Integer Format (10000 = 100%)
16 | 16 | Molar Analysis - C3 | 403817 | Scaled Integer Format (10000 = 100%)
17 | 16 | Molar Analysis - H2O | 403818 | Scaled Integer Format (10000 = 100%)
18 | 16 | Molar Analysis - H2S | 403819 | Scaled Integer Format (10000 = 100%)
19 | 16 | Molar Analysis - H2 | 403820 | Scaled Integer Format (10000 = 100%)
20 | 16 | Molar Analysis - CO | 403821 | Scaled Integer Format (10000 = 100%)
21 | 16 | Molar Analysis - O2 | 403822 | Scaled Integer Format (10000 = 100%)
22 | 16 | Molar Analysis - iC4 | 403823 | Scaled Integer Format (10000 = 100%)
23 | 16 | Molar Analysis - C4 | 403824 | Scaled Integer Format (10000 = 100%)
24 | 16 | Molar Analysis - iC5 | 403825 | Scaled Integer Format (10000 = 100%)
25 | 16 | Molar Analysis - C5 | 403826 | Scaled Integer Format (10000 = 100%)
26 | 16 | Molar Analysis - C6 | 403827 | Scaled Integer Format (10000 = 100%)
27 | 16 | Molar Analysis - C7 | 403828 | Scaled Integer Format (10000 = 100%)
28 | 16 | Molar Analysis - C8 | 403829 | Scaled Integer Format (10000 = 100%)
29 | 16 | Molar Analysis - C9 | 403830 | Scaled Integer Format (10000 = 100%)
30 | 16 | Molar Analysis - C10 | 403831 | Scaled Integer Format (10000 = 100%)
31 | 16 | Molar Analysis - He | 403832 | Scaled Integer Format (10000 = 100%)
32 | 16 | Molar Analysis - Ar | 403833 | Scaled Integer Format (10000 = 100%)
33 | 16 | Molar Analysis - C5 (neo-p) | 403834 | Scaled Integer Format (10000 = 100%)
34 | 16 | Molar Analysis - Ux | 403835 | Scaled Integer Format (10000 = 100%)
35 | 16 | Molar Analysis - Uy | 403836 | Scaled Integer Format (10000 = 100%)
36 | 16 | Meter Signals - Reserved | 403837
37 | 16 | Meter Signals - Reserved | 403838
38 | 16 | Meter Signals - Reserved | 403839
39 | 16 | Meter Signals - Reserved | 403840
40 | 16 | Meter Signals - Reset Acc 1 | 403841
41 | 16 | Meter Signals - Reset Acc 2 | 403842
42 | 16 | Meter Signals - Reset Acc 3 | 403843
43 | 16 | Meter Signals - Reset Acc 4 | 403844
44 | 16 | Write Daily Archive | 403845
45 | 16 | Write Hourly Archive | 403846
46 | 16 | Meter Signals - Reserved | 403847
47 | 16 | Meter Signals - Reserved | 403848
48 | 16 | Meter Signals - Reserved | 403849
49 | 16 | Meter Signals - Reserved | 403850
50 | 16 | Meter Signals - Reserved | 403851
51 | 16 | Meter Signals - Reserved | 403852
52 | 16 | Analysis is Present | 403853
53 | 16 | Meter Archive Record Fetch | 403854 | (=0 signal not present)
54 | 16 | Meter Archive Record Age | 403855 | (=0 current)
55 | 16 | Meter Archive File Select | 403856 | (=0 daily, 1=hourly)

## Meter Results -Pulse & Liquid
Meter 1 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 1 | Scan Count: process input | 400901
1 | 1 | Scan Count: calculation | 400902
2 | 1 | Meter in Alarm | 400903 | 0=no alarm
3 | 1 | Reserved | 400904
4 | 1 | Net Accumulator | 400905 | Long Integer Format
5 | 1 | Net Accumulator | 400906 | Long Integer Format
6 | 1 | Net Flow Rate | 400907 | Floating Point Format
7 | 1 | Net Flow Rate | 400908 | Floating Point Format
8 | 1 | Gross Accumulator | 400909 | Long Integer Format
9 | 1 | Gross Accumulator | 400910 | Long Integer Format
10 | 1 | Gross Standard Accumulator | 400911 | Long Integer Format
11 | 1 | Gross Standard Accumulator | 400912 | Long Integer Format
12 | 1 | Mass Accumulator | 400913 | Long Integer Format
13 | 1 | Mass Accumulator | 400914 | Long Integer Format
14 | 1 | Reserved | 400915
15 | 1 | Reserved | 400916
16 | 1 | Reserved | 400917
17 | 1 | Reserved | 400918
18 | 1 | Reserved | 400919
19 | 1 | Reserved | 400920
20 | 1 | Reserved | 400921
21 | 1 | Reserved | 400922
22 | 1 | Reserved | 400923
23 | 1 | Reserved | 400924
24 | 1 | Reserved | 400925
25 | 1 | Reserved | 400926
26 | 1 | Reserved | 400927
27 | 1 | Reserved | 400928
28 | 1 | Reserved | 400929
29 | 1 | Reserved | 400930
30 | 1 | Reserved | 400931
31 | 1 | Reserved | 400932
32 | 1 | Reserved | 400933
33 | 1 | Reserved | 400934
34 | 1 | Reserved | 400935
35 | 1 | Reserved | 400936
36 | 1 | Reserved | 400937
37 | 1 | Reserved | 400938
Meter 2 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 2 | Scan Count: process input | 401101
1 | 2 | Scan Count: calculation | 401102
2 | 2 | Meter in Alarm | 401103 | 0=no alarm
3 | 2 | Reserved | 401104
4 | 2 | Net Accumulator | 401105 | Long Integer Format
5 | 2 | Net Accumulator | 401106 | Long Integer Format
6 | 2 | Net Flow Rate | 401107 | Floating Point Format
7 | 2 | Net Flow Rate | 401108 | Floating Point Format
8 | 2 | Gross Accumulator | 401109 | Long Integer Format
9 | 2 | Gross Accumulator | 401110 | Long Integer Format
10 | 2 | Gross Standard Accumulator | 401111 | Long Integer Format
11 | 2 | Gross Standard Accumulator | 401112 | Long Integer Format
12 | 2 | Mass Accumulator | 401113 | Long Integer Format
13 | 2 | Mass Accumulator | 401114 | Long Integer Format
14 | 2 | Reserved | 401115
15 | 2 | Reserved | 401116
16 | 2 | Reserved | 401117
17 | 2 | Reserved | 401118
18 | 2 | Reserved | 401119
19 | 2 | Reserved | 401120
20 | 2 | Reserved | 401121
21 | 2 | Reserved | 401122
22 | 2 | Reserved | 401123
23 | 2 | Reserved | 401124
24 | 2 | Reserved | 401125
25 | 2 | Reserved | 401126
26 | 2 | Reserved | 401127
27 | 2 | Reserved | 401128
28 | 2 | Reserved | 401129
29 | 2 | Reserved | 401130
30 | 2 | Reserved | 401131
31 | 2 | Reserved | 401132
32 | 2 | Reserved | 401133
33 | 2 | Reserved | 401134
34 | 2 | Reserved | 401135
35 | 2 | Reserved | 401136
36 | 2 | Reserved | 401137
37 | 2 | Reserved | 401138
Meter 3 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 3 | Scan Count: process input | 401301
1 | 3 | Scan Count: calculation | 401302
2 | 3 | Meter in Alarm | 401303 | 0=no alarm
3 | 3 | Reserved | 401304
4 | 3 | Net Accumulator | 401305 | Long Integer Format
5 | 3 | Net Accumulator | 401306 | Long Integer Format
6 | 3 | Net Flow Rate | 401307 | Floating Point Format
7 | 3 | Net Flow Rate | 401308 | Floating Point Format
8 | 3 | Gross Accumulator | 401309 | Long Integer Format
9 | 3 | Gross Accumulator | 401310 | Long Integer Format
10 | 3 | Gross Standard Accumulator | 401311 | Long Integer Format
11 | 3 | Gross Standard Accumulator | 401312 | Long Integer Format
12 | 3 | Mass Accumulator | 401313 | Long Integer Format
13 | 3 | Mass Accumulator | 401314 | Long Integer Format
14 | 3 | Reserved | 401315
15 | 3 | Reserved | 401316
16 | 3 | Reserved | 401317
17 | 3 | Reserved | 401318
18 | 3 | Reserved | 401319
19 | 3 | Reserved | 401320
20 | 3 | Reserved | 401321
21 | 3 | Reserved | 401322
22 | 3 | Reserved | 401323
23 | 3 | Reserved | 401324
24 | 3 | Reserved | 401325
25 | 3 | Reserved | 401326
26 | 3 | Reserved | 401327
27 | 3 | Reserved | 401328
28 | 3 | Reserved | 401329
29 | 3 | Reserved | 401330
30 | 3 | Reserved | 401331
31 | 3 | Reserved | 401332
32 | 3 | Reserved | 401333
33 | 3 | Reserved | 401334
34 | 3 | Reserved | 401335
35 | 3 | Reserved | 401336
36 | 3 | Reserved | 401337
37 | 3 | Reserved | 401338
Meter 4 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 4 | Scan Count: process input | 401501
1 | 4 | Scan Count: calculation | 401502
2 | 4 | Meter in Alarm | 401503 | 0=no alarm
3 | 4 | Reserved | 401504
4 | 4 | Net Accumulator | 401505 | Long Integer Format
5 | 4 | Net Accumulator | 401506 | Long Integer Format
6 | 4 | Net Flow Rate | 401507 | Floating Point Format
7 | 4 | Net Flow Rate | 401508 | Floating Point Format
8 | 4 | Gross Accumulator | 401509 | Long Integer Format
9 | 4 | Gross Accumulator | 401510 | Long Integer Format
10 | 4 | Gross Standard Accumulator | 401511 | Long Integer Format
11 | 4 | Gross Standard Accumulator | 401512 | Long Integer Format
12 | 4 | Mass Accumulator | 401513 | Long Integer Format
13 | 4 | Mass Accumulator | 401514 | Long Integer Format
14 | 4 | Reserved | 401515
15 | 4 | Reserved | 401516
16 | 4 | Reserved | 401517
17 | 4 | Reserved | 401518
18 | 4 | Reserved | 401519
19 | 4 | Reserved | 401520
20 | 4 | Reserved | 401521
21 | 4 | Reserved | 401522
22 | 4 | Reserved | 401523
23 | 4 | Reserved | 401524
24 | 4 | Reserved | 401525
25 | 4 | Reserved | 401526
26 | 4 | Reserved | 401527
27 | 4 | Reserved | 401528
28 | 4 | Reserved | 401529
29 | 4 | Reserved | 401530
30 | 4 | Reserved | 401531
31 | 4 | Reserved | 401532
32 | 4 | Reserved | 401533
33 | 4 | Reserved | 401534
34 | 4 | Reserved | 401535
35 | 4 | Reserved | 401536
36 | 4 | Reserved | 401537
37 | 4 | Reserved | 401538
Meter 5 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 5 | Scan Count: process input | 401701
1 | 5 | Scan Count: calculation | 401702
2 | 5 | Meter in Alarm | 401703 | 0=no alarm
3 | 5 | Reserved | 401704
4 | 5 | Net Accumulator | 401705 | Long Integer Format
5 | 5 | Net Accumulator | 401706 | Long Integer Format
6 | 5 | Net Flow Rate | 401707 | Floating Point Format
7 | 5 | Net Flow Rate | 401708 | Floating Point Format
8 | 5 | Gross Accumulator | 401709 | Long Integer Format
9 | 5 | Gross Accumulator | 401710 | Long Integer Format
10 | 5 | Gross Standard Accumulator | 401711 | Long Integer Format
11 | 5 | Gross Standard Accumulator | 401712 | Long Integer Format
12 | 5 | Mass Accumulator | 401713 | Long Integer Format
13 | 5 | Mass Accumulator | 401714 | Long Integer Format
14 | 5 | Reserved | 401715
15 | 5 | Reserved | 401716
16 | 5 | Reserved | 401717
17 | 5 | Reserved | 401718
18 | 5 | Reserved | 401719
19 | 5 | Reserved | 401720
20 | 5 | Reserved | 401721
21 | 5 | Reserved | 401722
22 | 5 | Reserved | 401723
23 | 5 | Reserved | 401724
24 | 5 | Reserved | 401725
25 | 5 | Reserved | 401726
26 | 5 | Reserved | 401727
27 | 5 | Reserved | 401728
28 | 5 | Reserved | 401729
29 | 5 | Reserved | 401730
30 | 5 | Reserved | 401731
31 | 5 | Reserved | 401732
32 | 5 | Reserved | 401733
33 | 5 | Reserved | 401734
34 | 5 | Reserved | 401735
35 | 5 | Reserved | 401736
36 | 5 | Reserved | 401737
37 | 5 | Reserved | 401738
Meter 6 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 6 | Scan Count: process input | 401901
1 | 6 | Scan Count: calculation | 401902
2 | 6 | Meter in Alarm | 401903 | 0=no alarm
3 | 6 | Reserved | 401904
4 | 6 | Net Accumulator | 401905 | Long Integer Format
5 | 6 | Net Accumulator | 401906 | Long Integer Format
6 | 6 | Net Flow Rate | 401907 | Floating Point Format
7 | 6 | Net Flow Rate | 401908 | Floating Point Format
8 | 6 | Gross Accumulator | 401909 | Long Integer Format
9 | 6 | Gross Accumulator | 401910 | Long Integer Format
10 | 6 | Gross Standard Accumulator | 401911 | Long Integer Format
11 | 6 | Gross Standard Accumulator | 401912 | Long Integer Format
12 | 6 | Mass Accumulator | 401913 | Long Integer Format
13 | 6 | Mass Accumulator | 401914 | Long Integer Format
14 | 6 | Reserved | 401915
15 | 6 | Reserved | 401916
16 | 6 | Reserved | 401917
17 | 6 | Reserved | 401918
18 | 6 | Reserved | 401919
19 | 6 | Reserved | 401920
20 | 6 | Reserved | 401921
21 | 6 | Reserved | 401922
22 | 6 | Reserved | 401923
23 | 6 | Reserved | 401924
24 | 6 | Reserved | 401925
25 | 6 | Reserved | 401926
26 | 6 | Reserved | 401927
27 | 6 | Reserved | 401928
28 | 6 | Reserved | 401929
29 | 6 | Reserved | 401930
30 | 6 | Reserved | 401931
31 | 6 | Reserved | 401932
32 | 6 | Reserved | 401933
33 | 6 | Reserved | 401934
34 | 6 | Reserved | 401935
35 | 6 | Reserved | 401936
36 | 6 | Reserved | 401937
37 | 6 | Reserved | 401938
Meter 7 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 7 | Scan Count: process input | 402101
1 | 7 | Scan Count: calculation | 402102
2 | 7 | Meter in Alarm | 402103 | 0=no alarm
3 | 7 | Reserved | 402104
4 | 7 | Net Accumulator | 402105 | Long Integer Format
5 | 7 | Net Accumulator | 402106 | Long Integer Format
6 | 7 | Net Flow Rate | 402107 | Floating Point Format
7 | 7 | Net Flow Rate | 402108 | Floating Point Format
8 | 7 | Gross Accumulator | 402109 | Long Integer Format
9 | 7 | Gross Accumulator | 402110 | Long Integer Format
10 | 7 | Gross Standard Accumulator | 402111 | Long Integer Format
11 | 7 | Gross Standard Accumulator | 402112 | Long Integer Format
12 | 7 | Mass Accumulator | 402113 | Long Integer Format
13 | 7 | Mass Accumulator | 402114 | Long Integer Format
14 | 7 | Reserved | 402115
15 | 7 | Reserved | 402116
16 | 7 | Reserved | 402117
17 | 7 | Reserved | 402118
18 | 7 | Reserved | 402119
19 | 7 | Reserved | 402120
20 | 7 | Reserved | 402121
21 | 7 | Reserved | 402122
22 | 7 | Reserved | 402123
23 | 7 | Reserved | 402124
24 | 7 | Reserved | 402125
25 | 7 | Reserved | 402126
26 | 7 | Reserved | 402127
27 | 7 | Reserved | 402128
28 | 7 | Reserved | 402129
29 | 7 | Reserved | 402130
30 | 7 | Reserved | 402131
31 | 7 | Reserved | 402132
32 | 7 | Reserved | 402133
33 | 7 | Reserved | 402134
34 | 7 | Reserved | 402135
35 | 7 | Reserved | 402136
36 | 7 | Reserved | 402137
37 | 7 | Reserved | 402138
Meter 8 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 8 | Scan Count: process input | 402301
1 | 8 | Scan Count: calculation | 402302
2 | 8 | Meter in Alarm | 402303 | 0=no alarm
3 | 8 | Reserved | 402304
4 | 8 | Net Accumulator | 402305 | Long Integer Format
5 | 8 | Net Accumulator | 402306 | Long Integer Format
6 | 8 | Net Flow Rate | 402307 | Floating Point Format
7 | 8 | Net Flow Rate | 402308 | Floating Point Format
8 | 8 | Gross Accumulator | 402309 | Long Integer Format
9 | 8 | Gross Accumulator | 402310 | Long Integer Format
10 | 8 | Gross Standard Accumulator | 402311 | Long Integer Format
11 | 8 | Gross Standard Accumulator | 402312 | Long Integer Format
12 | 8 | Mass Accumulator | 402313 | Long Integer Format
13 | 8 | Mass Accumulator | 402314 | Long Integer Format
14 | 8 | Reserved | 402315
15 | 8 | Reserved | 402316
16 | 8 | Reserved | 402317
17 | 8 | Reserved | 402318
18 | 8 | Reserved | 402319
19 | 8 | Reserved | 402320
20 | 8 | Reserved | 402321
21 | 8 | Reserved | 402322
22 | 8 | Reserved | 402323
23 | 8 | Reserved | 402324
24 | 8 | Reserved | 402325
25 | 8 | Reserved | 402326
26 | 8 | Reserved | 402327
27 | 8 | Reserved | 402328
28 | 8 | Reserved | 402329
29 | 8 | Reserved | 402330
30 | 8 | Reserved | 402331
31 | 8 | Reserved | 402332
32 | 8 | Reserved | 402333
33 | 8 | Reserved | 402334
34 | 8 | Reserved | 402335
35 | 8 | Reserved | 402336
36 | 8 | Reserved | 402337
37 | 8 | Reserved | 402338
Meter 9 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 9 | Scan Count: process input | 402501
1 | 9 | Scan Count: calculation | 402502
2 | 9 | Meter in Alarm | 402503 | 0=no alarm
3 | 9 | Reserved | 402504
4 | 9 | Net Accumulator | 402505 | Long Integer Format
5 | 9 | Net Accumulator | 402506 | Long Integer Format
6 | 9 | Net Flow Rate | 402507 | Floating Point Format
7 | 9 | Net Flow Rate | 402508 | Floating Point Format
8 | 9 | Gross Accumulator | 402509 | Long Integer Format
9 | 9 | Gross Accumulator | 402510 | Long Integer Format
10 | 9 | Gross Standard Accumulator | 402511 | Long Integer Format
11 | 9 | Gross Standard Accumulator | 402512 | Long Integer Format
12 | 9 | Mass Accumulator | 402513 | Long Integer Format
13 | 9 | Mass Accumulator | 402514 | Long Integer Format
14 | 9 | Reserved | 402515
15 | 9 | Reserved | 402516
16 | 9 | Reserved | 402517
17 | 9 | Reserved | 402518
18 | 9 | Reserved | 402519
19 | 9 | Reserved | 402520
20 | 9 | Reserved | 402521
21 | 9 | Reserved | 402522
22 | 9 | Reserved | 402523
23 | 9 | Reserved | 402524
24 | 9 | Reserved | 402525
25 | 9 | Reserved | 402526
26 | 9 | Reserved | 402527
27 | 9 | Reserved | 402528
28 | 9 | Reserved | 402529
29 | 9 | Reserved | 402530
30 | 9 | Reserved | 402531
31 | 9 | Reserved | 402532
32 | 9 | Reserved | 402533
33 | 9 | Reserved | 402534
34 | 9 | Reserved | 402535
35 | 9 | Reserved | 402536
36 | 9 | Reserved | 402537
37 | 9 | Reserved | 402538
Meter 10 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 10 | Scan Count: process input | 402701
1 | 10 | Scan Count: calculation | 402702
2 | 10 | Meter in Alarm | 402703 | 0=no alarm
3 | 10 | Reserved | 402704
4 | 10 | Net Accumulator | 402705 | Long Integer Format
5 | 10 | Net Accumulator | 402706 | Long Integer Format
6 | 10 | Net Flow Rate | 402707 | Floating Point Format
7 | 10 | Net Flow Rate | 402708 | Floating Point Format
8 | 10 | Gross Accumulator | 402709 | Long Integer Format
9 | 10 | Gross Accumulator | 402710 | Long Integer Format
10 | 10 | Gross Standard Accumulator | 402711 | Long Integer Format
11 | 10 | Gross Standard Accumulator | 402712 | Long Integer Format
12 | 10 | Mass Accumulator | 402713 | Long Integer Format
13 | 10 | Mass Accumulator | 402714 | Long Integer Format
14 | 10 | Reserved | 402715
15 | 10 | Reserved | 402716
16 | 10 | Reserved | 402717
17 | 10 | Reserved | 402718
18 | 10 | Reserved | 402719
19 | 10 | Reserved | 402720
20 | 10 | Reserved | 402721
21 | 10 | Reserved | 402722
22 | 10 | Reserved | 402723
23 | 10 | Reserved | 402724
24 | 10 | Reserved | 402725
25 | 10 | Reserved | 402726
26 | 10 | Reserved | 402727
27 | 10 | Reserved | 402728
28 | 10 | Reserved | 402729
29 | 10 | Reserved | 402730
30 | 10 | Reserved | 402731
31 | 10 | Reserved | 402732
32 | 10 | Reserved | 402733
33 | 10 | Reserved | 402734
34 | 10 | Reserved | 402735
35 | 10 | Reserved | 402736
36 | 10 | Reserved | 402737
37 | 10 | Reserved | 402738
Meter 11 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 11 | Scan Count: process input | 402901
1 | 11 | Scan Count: calculation | 402902
2 | 11 | Meter in Alarm | 402903 | 0=no alarm
3 | 11 | Reserved | 402904
4 | 11 | Net Accumulator | 402905 | Long Integer Format
5 | 11 | Net Accumulator | 402906 | Long Integer Format
6 | 11 | Net Flow Rate | 402907 | Floating Point Format
7 | 11 | Net Flow Rate | 402908 | Floating Point Format
8 | 11 | Gross Accumulator | 402909 | Long Integer Format
9 | 11 | Gross Accumulator | 402910 | Long Integer Format
10 | 11 | Gross Standard Accumulator | 402911 | Long Integer Format
11 | 11 | Gross Standard Accumulator | 402912 | Long Integer Format
12 | 11 | Mass Accumulator | 402913 | Long Integer Format
13 | 11 | Mass Accumulator | 402914 | Long Integer Format
14 | 11 | Reserved | 402915
15 | 11 | Reserved | 402916
16 | 11 | Reserved | 402917
17 | 11 | Reserved | 402918
18 | 11 | Reserved | 402919
19 | 11 | Reserved | 402920
20 | 11 | Reserved | 402921
21 | 11 | Reserved | 402922
22 | 11 | Reserved | 402923
23 | 11 | Reserved | 402924
24 | 11 | Reserved | 402925
25 | 11 | Reserved | 402926
26 | 11 | Reserved | 402927
27 | 11 | Reserved | 402928
28 | 11 | Reserved | 402929
29 | 11 | Reserved | 402930
30 | 11 | Reserved | 402931
31 | 11 | Reserved | 402932
32 | 11 | Reserved | 402933
33 | 11 | Reserved | 402934
34 | 11 | Reserved | 402935
35 | 11 | Reserved | 402936
36 | 11 | Reserved | 402937
37 | 11 | Reserved | 402938
Meter 12 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 12 | Scan Count: process input | 403101
1 | 12 | Scan Count: calculation | 403102
2 | 12 | Meter in Alarm | 403103 | 0=no alarm
3 | 12 | Reserved | 403104
4 | 12 | Net Accumulator | 403105 | Long Integer Format
5 | 12 | Net Accumulator | 403106 | Long Integer Format
6 | 12 | Net Flow Rate | 403107 | Floating Point Format
7 | 12 | Net Flow Rate | 403108 | Floating Point Format
8 | 12 | Gross Accumulator | 403109 | Long Integer Format
9 | 12 | Gross Accumulator | 403110 | Long Integer Format
10 | 12 | Gross Standard Accumulator | 403111 | Long Integer Format
11 | 12 | Gross Standard Accumulator | 403112 | Long Integer Format
12 | 12 | Mass Accumulator | 403113 | Long Integer Format
13 | 12 | Mass Accumulator | 403114 | Long Integer Format
14 | 12 | Reserved | 403115
15 | 12 | Reserved | 403116
16 | 12 | Reserved | 403117
17 | 12 | Reserved | 403118
18 | 12 | Reserved | 403119
19 | 12 | Reserved | 403120
20 | 12 | Reserved | 403121
21 | 12 | Reserved | 403122
22 | 12 | Reserved | 403123
23 | 12 | Reserved | 403124
24 | 12 | Reserved | 403125
25 | 12 | Reserved | 403126
26 | 12 | Reserved | 403127
27 | 12 | Reserved | 403128
28 | 12 | Reserved | 403129
29 | 12 | Reserved | 403130
30 | 12 | Reserved | 403131
31 | 12 | Reserved | 403132
32 | 12 | Reserved | 403133
33 | 12 | Reserved | 403134
34 | 12 | Reserved | 403135
35 | 12 | Reserved | 403136
36 | 12 | Reserved | 403137
37 | 12 | Reserved | 403138
Meter 13 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 13 | Scan Count: process input | 403301
1 | 13 | Scan Count: calculation | 403302
2 | 13 | Meter in Alarm | 403303 | 0=no alarm
3 | 13 | Reserved | 403304
4 | 13 | Net Accumulator | 403305 | Long Integer Format
5 | 13 | Net Accumulator | 403306 | Long Integer Format
6 | 13 | Net Flow Rate | 403307 | Floating Point Format
7 | 13 | Net Flow Rate | 403308 | Floating Point Format
8 | 13 | Gross Accumulator | 403309 | Long Integer Format
9 | 13 | Gross Accumulator | 403310 | Long Integer Format
10 | 13 | Gross Standard Accumulator | 403311 | Long Integer Format
11 | 13 | Gross Standard Accumulator | 403312 | Long Integer Format
12 | 13 | Mass Accumulator | 403313 | Long Integer Format
13 | 13 | Mass Accumulator | 403314 | Long Integer Format
14 | 13 | Reserved | 403315
15 | 13 | Reserved | 403316
16 | 13 | Reserved | 403317
17 | 13 | Reserved | 403318
18 | 13 | Reserved | 403319
19 | 13 | Reserved | 403320
20 | 13 | Reserved | 403321
21 | 13 | Reserved | 403322
22 | 13 | Reserved | 403323
23 | 13 | Reserved | 403324
24 | 13 | Reserved | 403325
25 | 13 | Reserved | 403326
26 | 13 | Reserved | 403327
27 | 13 | Reserved | 403328
28 | 13 | Reserved | 403329
29 | 13 | Reserved | 403330
30 | 13 | Reserved | 403331
31 | 13 | Reserved | 403332
32 | 13 | Reserved | 403333
33 | 13 | Reserved | 403334
34 | 13 | Reserved | 403335
35 | 13 | Reserved | 403336
36 | 13 | Reserved | 403337
37 | 13 | Reserved | 403338
Meter 14 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 14 | Scan Count: process input | 403501
1 | 14 | Scan Count: calculation | 403502
2 | 14 | Meter in Alarm | 403503 | 0=no alarm
3 | 14 | Reserved | 403504
4 | 14 | Net Accumulator | 403505 | Long Integer Format
5 | 14 | Net Accumulator | 403506 | Long Integer Format
6 | 14 | Net Flow Rate | 403507 | Floating Point Format
7 | 14 | Net Flow Rate | 403508 | Floating Point Format
8 | 14 | Gross Accumulator | 403509 | Long Integer Format
9 | 14 | Gross Accumulator | 403510 | Long Integer Format
10 | 14 | Gross Standard Accumulator | 403511 | Long Integer Format
11 | 14 | Gross Standard Accumulator | 403512 | Long Integer Format
12 | 14 | Mass Accumulator | 403513 | Long Integer Format
13 | 14 | Mass Accumulator | 403514 | Long Integer Format
14 | 14 | Reserved | 403515
15 | 14 | Reserved | 403516
16 | 14 | Reserved | 403517
17 | 14 | Reserved | 403518
18 | 14 | Reserved | 403519
19 | 14 | Reserved | 403520
20 | 14 | Reserved | 403521
21 | 14 | Reserved | 403522
22 | 14 | Reserved | 403523
23 | 14 | Reserved | 403524
24 | 14 | Reserved | 403525
25 | 14 | Reserved | 403526
26 | 14 | Reserved | 403527
27 | 14 | Reserved | 403528
28 | 14 | Reserved | 403529
29 | 14 | Reserved | 403530
30 | 14 | Reserved | 403531
31 | 14 | Reserved | 403532
32 | 14 | Reserved | 403533
33 | 14 | Reserved | 403534
34 | 14 | Reserved | 403535
35 | 14 | Reserved | 403536
36 | 14 | Reserved | 403537
37 | 14 | Reserved | 403538
Meter 15 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 15 | Scan Count: process input | 403701
1 | 15 | Scan Count: calculation | 403702
2 | 15 | Meter in Alarm | 403703 | 0=no alarm
3 | 15 | Reserved | 403704
4 | 15 | Net Accumulator | 403705 | Long Integer Format
5 | 15 | Net Accumulator | 403706 | Long Integer Format
6 | 15 | Net Flow Rate | 403707 | Floating Point Format
7 | 15 | Net Flow Rate | 403708 | Floating Point Format
8 | 15 | Gross Accumulator | 403709 | Long Integer Format
9 | 15 | Gross Accumulator | 403710 | Long Integer Format
10 | 15 | Gross Standard Accumulator | 403711 | Long Integer Format
11 | 15 | Gross Standard Accumulator | 403712 | Long Integer Format
12 | 15 | Mass Accumulator | 403713 | Long Integer Format
13 | 15 | Mass Accumulator | 403714 | Long Integer Format
14 | 15 | Reserved | 403715
15 | 15 | Reserved | 403716
16 | 15 | Reserved | 403717
17 | 15 | Reserved | 403718
18 | 15 | Reserved | 403719
19 | 15 | Reserved | 403720
20 | 15 | Reserved | 403721
21 | 15 | Reserved | 403722
22 | 15 | Reserved | 403723
23 | 15 | Reserved | 403724
24 | 15 | Reserved | 403725
25 | 15 | Reserved | 403726
26 | 15 | Reserved | 403727
27 | 15 | Reserved | 403728
28 | 15 | Reserved | 403729
29 | 15 | Reserved | 403730
30 | 15 | Reserved | 403731
31 | 15 | Reserved | 403732
32 | 15 | Reserved | 403733
33 | 15 | Reserved | 403734
34 | 15 | Reserved | 403735
35 | 15 | Reserved | 403736
36 | 15 | Reserved | 403737
37 | 15 | Reserved | 403738
Meter 16 Results Pulse & Liquid
Offset | Meter # | Description | Word Address | Comments
0 | 16 | Scan Count: process input | 403901
1 | 16 | Scan Count: calculation | 403902
2 | 16 | Meter in Alarm | 403903 | 0=no alarm
3 | 16 | Reserved | 403904
4 | 16 | Net Accumulator | 403905 | Long Integer Format
5 | 16 | Net Accumulator | 403906 | Long Integer Format
6 | 16 | Net Flow Rate | 403907 | Floating Point Format
7 | 16 | Net Flow Rate | 403908 | Floating Point Format
8 | 16 | Gross Accumulator | 403909 | Long Integer Format
9 | 16 | Gross Accumulator | 403910 | Long Integer Format
10 | 16 | Gross Standard Accumulator | 403911 | Long Integer Format
11 | 16 | Gross Standard Accumulator | 403912 | Long Integer Format
12 | 16 | Mass Accumulator | 403913 | Long Integer Format
13 | 16 | Mass Accumulator | 403914 | Long Integer Format
14 | 16 | Reserved | 403915
15 | 16 | Reserved | 403916
16 | 16 | Reserved | 403917
17 | 16 | Reserved | 403918
18 | 16 | Reserved | 403919
19 | 16 | Reserved | 403920
20 | 16 | Reserved | 403921
21 | 16 | Reserved | 403922
22 | 16 | Reserved | 403923
23 | 16 | Reserved | 403924
24 | 16 | Reserved | 403925
25 | 16 | Reserved | 403926
26 | 16 | Reserved | 403927
27 | 16 | Reserved | 403928
28 | 16 | Reserved | 403929
29 | 16 | Reserved | 403930
30 | 16 | Reserved | 403931
31 | 16 | Reserved | 403932
32 | 16 | Reserved | 403933
33 | 16 | Reserved | 403934
34 | 16 | Reserved | 403935
35 | 16 | Reserved | 403936
36 | 16 | Reserved | 403937
37 | 16 | Reserved | 403938